## KAZ PP Project Risk Register
KAZ POWER PLANT UPGRADE PROJECT — PROJECT-LEVEL RISK REGISTER (v1 — 14.09.2026 — companion to corrected JHA Rev 1)
Scope note: the JHA (KAZ Project Risk Analysis 12 Corrected) covers job-level EHS hazards only. This register covers program-level risks of a power-plant EXPANSION at a live station (Khur Al Zubair, Basrah). Rating: R = L × S; 1–7 Low / 8–12 Medium / 13–25 High. L: 1 Very Unlikely → 5 Certain. S: 1 No impact → 5 Fatal / catastrophic (cost, production, schedule).
ID | Risk Category | Risk Description | Potential Consequence | L (1-5) | S (1-5) | R | Rating | Risk Owner | Mitigation Plan (prevention) | Contingency Plan (response) | Residual R (target ≤12) & Status
P1 | Procurement / Supply | Delay of long-lead equipment (turbine parts, generator, transformer, switchgear) due to manufacturer backlog or logistics | Schedule slip of critical path; liquidated damages | 3 | 5 | 15 | HIGH | 【TO BE ASSIGNED — Procurement Manager】 | Place long-lead orders immediately; on-site expediting; approve alternate sources; verify factory acceptance test (FAT) dates against schedule; buffer in the master schedule | Partial deliveries; air freight for critical items; re-sequence work packages; formal extension claim if force majeure | Target 10 (M) — OPEN
P2 | Grid Interconnection | Synchronization failure / grid-code non-compliance: protection mis-coordination, reverse power, islanding, connection permit delay | Failed sync tests; grid operator rejection; production delay; safety risk on grid | 3 | 4 | 12 | MEDIUM | 【TO BE ASSIGNED — Electrical/Commissioning Manager】 | Early coordination with the grid operator & Ministry of Electricity; protection & coordination studies; relay setting review; synchronization test plan with hold points; grid-code compliance documentation | Extend test phase; re-study protection settings; dedicated grid-interface meeting per test campaign | Target 8 (M) — OPEN
P3 | Interface with Live Plant | Work interface with the operating station (BGC & MOE operated): outage windows not honored, live parts, shared utilities, production interruption | Production loss liability; injury from live parts; schedule conflicts | 3 | 4 | 12 | MEDIUM | 【TO BE ASSIGNED — Project Manager】 | Joint JHA with plant operators (BGC & MOE) under SE coordination; agreed outage/blackout windows; single PTW authority = Siemens Energy (verified); live-area map; daily interface meeting; permanent barricades around live parts | Stop-work authority; shift work to off-peak windows; liability insurance invoked; client escalation | Target 8 (M) — OPEN (inherently medium)
P4 | Commissioning | Hot commissioning deviations: turbine start/run-up/load issues, gas system leaks, oil leaks | Turbine damage; fire; delayed COD; rework cost | 3 | 4 | 12 | MEDIUM | 【TO BE ASSIGNED — Commissioning Manager】 | OEM procedures step-by-step with hold points; qualified test team (OEM + contractor); gas-free & LEL monitoring; oil leak checks per stage; defined acceptance criteria | OEM support escalation; root-cause analysis; spares on site; revised test plan | Target 8 (M) — OPEN
P5 | Permitting / Regulatory | Customs clearance delay for equipment at Basra/Umm Qasr; missing environmental or local permits | Equipment stuck at port; storage cost; schedule slip | 3 | 3 | 9 | MEDIUM | 【TO BE ASSIGNED — Contracts/Logistics】 | Start permit applications early; local customs agent; document checklist before shipping; engage client for government relations; pre-clear documentation | Split shipments; bonded storage; client escalation to authorities | Target 6 (L) — OPEN
P6 | Security / Geopolitical | Security incident at site or during travel (Basrah, Iraq): theft, civil disturbance, regional escalation | Injury/casualty; site shutdown; evacuation | 3 | 4 | 12 | MEDIUM | 【TO BE ASSIGNED — Security/HSE Manager】 | Site security plan per client & SE requirements; access control & patrols; safe room; redundant communications; travel control & escort; insurance; regional situation monitoring | Evacuation plan execution; shelter in place; security force escalation; insurance claim | Target 8 (M) — OPEN (inherently medium)
P7 | Financial | IQD currency fluctuation; payment delays; inflation of local costs | Margin erosion; cash-flow strain on subcontractors | 3 | 3 | 9 | MEDIUM | 【TO BE ASSIGNED — Finance】 | Contract currency clause; payment schedule enforcement; hedging for large exposures; monthly cash-flow review | Contract renegotiation per variation/adjustment clause; payment escalation | Target 6 (L) — OPEN
P8 | Subcontracting | Subcontractor performance (AL-MIAL Company); single-point dependency on a critical trade | Quality/schedule impact; rework; penalty exposure | 3 | 3 | 9 | MEDIUM | 【TO BE ASSIGNED — Project Controls】 | Qualified prequalification; KPI & performance monitoring; milestone payments; backup contractor qualified in parallel | Performance improvement plan; partial demobilization & replacement; claims management | Target 6 (L) — OPEN
P9 | Weather | Basra extreme summer heat (up to ~50°C) forcing work stoppage in outdoor/critical phases | Schedule compression; heat-related injuries; rework quality issues | 4 | 3 | 12 | MEDIUM | 【TO BE ASSIGNED — Construction Manager】 | Schedule outdoor work around cool hours (night/early morning); Heat Stress Protocol (active for summer operations: work/rest cycles, hydration, acclimatization); indoor-phase planning in summer; early procurement to de-bottleneck summer | Shift remaining outdoor packages to cooler months; night work; client agreement on weather-related schedule adjustment | Target 8 (M) — OPEN
P10 | Schedule / Commercial | Overall schedule delay (aggregation of above) triggering liquidated damages | LD exposure; contract penalties; relationship strain | 3 | 4 | 12 | MEDIUM | 【TO BE ASSIGNED — Project Manager】 | Critical-path management; weekly early-warning report; float monitoring; interface control with client outage windows; resource leveling | Recovery plan (catch-up shifts, additional crews); variation management; LD negotiation per contract | Target 8 (M) — OPEN
DOCUMENT CONTROL
Document No. | KAZ-PP-RR-001 | Rev. | 0 (initial — to be baselined) | Date | 14.09.2026
Prepared by | 【TO BE COMPLETED】 | Reviewed by | 【TO BE COMPLETED — EHS Manager】 | Approved by | 【TO BE COMPLETED — Project Manager】
Review frequency | 14.09.2026 — aligned with KAZPP Safety and Scope of Work Document (Rev 1) | Next review | 【TO BE SCHEDULED】 | Status | DRAFT FOR REVIEW

## Legend & Instructions
KAZ PP PROJECT RISK REGISTER — LEGEND & INSTRUCTIONS
Rating scale: R = L × S (5×5). Bands: 1–7 = LOW (acceptable, monitor) ¦ 8–12 = MEDIUM (acceptable with controls) ¦ 13–25 = HIGH (unacceptable — action required before exposure).
Likelihood L: 1 Very Unlikely ¦ 2 Unlikely ¦ 3 Likely ¦ 4 Very Likely ¦ 5 Certain
Severity S: 1 Negligible ¦ 2 Minor (cost < agreed limit, no production impact) ¦ 3 Moderate (cost/production impact ≤ 1 month) ¦ 4 Major (significant cost, production loss, major schedule slip) ¦ 5 Catastrophic (fatalities, plant damage, project failure)
Status values: OPEN ¦ IN PROGRESS ¦ CLOSED ¦ ACCEPTED
Every HIGH risk requires a named owner and a dated mitigation plan before the related work package is released.
Residual R target: ≤ 12 (Medium or lower) after controls, except risks accepted at project level with written approval.
Relationship to JHA: this register does NOT replace job-level JHAs. Each work package (e.g. critical lift, HV work, gas commissioning) must still have its own JHA issued per SE-FO-0023.