SIEMENS ENERGY — SE GT SU

KAZPP — Khor Al-Zubair Power Plant Upgrade / Extension Project

SAFETY AND SCOPE OF WORK DOCUMENT (Job Hazard Analysis — JHA)

| Document No: | 1 | Rev: | 1 | Date: | 14.09.2026 |
| --- | --- | --- | --- | --- | --- |
| Project | Khor Al-Zubair Power Plant Upgrade / Extension Project (KAZPP) |  |  |  |  |
| Main Client | Siemens Energy | Plant Operators | Basrah Gas Company (BGC) & Ministry of Electricity (MOE) | PTW Authority | SIEMENS ENERGY (exclusively) |
| Subcontractor | AL-MIAL Company | Location | Basrah, Iraq | Work Area | Khur Al Zubair Power Station |
| Key SE Site Personnel | Site Manager: Raed Al-Nidawi ¦ EHS Manager: Ahmed Mansour | Field Work Team | 60+ personnel — sign-off in Step 5 | Prepared by | AL-MIAL Company / SE GT SU |
| Activity / Scope of Work | Construction, Installation, Testing & Commissioning of the KAZPP upgrade/extension. INCLUDED HAZARDS (verified): (1) Hot work — welding & thermal cutting; (2) Natural gas system operations; (3) Critical lifting operations — detailed specifications as per approved Lifting Plan; (4) Pressure vessels; (5) Working within/near hazardous & explosive areas (ATEX). |  |  |  |  |
| Used Vehicles | Truck, Excavator | Used Equipment’s | Hand Tools, Power Tools, Lifting Equipment’s, Test Equipment’s, Manlift, Crane |  |  |

NOTE: If after risk evaluation and with all the necessary controls in place the risk rating (R) is HIGH (13–25), the EHS department is to be contacted for guidance on the task/process. Work permits are issued exclusively by SIEMENS ENERGY (verified PTW authority); plant operators BGC & MOE remain the operational interface for live areas.

EMERGENCY CONTACTS — VERIFIED LOCAL NUMBERS (previous international number removed per verified data)

| POLICE | FIRE (CIVIL DEFENSE) | AMBULANCE | UNIFIED EMERGENCY HOTLINE | NEAREST HOSPITAL | SITE FIRST AIDER |
| --- | --- | --- | --- | --- | --- |
| 104 | 115 | 122 | 911 | Al-Zubair General Hospital (travel time ~45 minutes) | Haider — +964 770 731 3604 |

REVISION NOTES — Rev 1 (14.09.2026)

1. Severity scale corrected: level 4 defined (Major Injury / Permanent Disability).

2. Risk matrix bands corrected: 1–7 Low / 8–12 Medium / 13–25 High (score 7 was previously unclassified).

3. Residual-risk logic corrected: controls reduce LIKELIHOOD (primary) and severity only where the worst outcome is genuinely eliminated (previously severity was mechanically set to 1 in every row).

4. Duplicate rows removed (old 11=12, 14=15); mismatched precautions fixed (old rows 7, 14, 15, 21); template remnants removed.

5. Management processes (STOP, Incident Management) removed from the risk matrix — tracked as EHS program KPIs, not hazards.

6. PTW authority verified and applied throughout: SIEMENS ENERGY exclusively; plant operators (BGC & MOE) are the operational interface for live areas; HV electrical controls are implemented by the executing subcontractor under SE direction (previously “by the customer”).

7. Missing site risks added, incl. those now confirmed in scope: Pressure Vessels (row 34) and Hazardous/Explosive (ATEX) Areas (row 35), plus heat stress, security, live-plant interface, critical lifts, gas operations, hot surfaces, spill, noise, dust, moving machinery, ergonomics, chemicals, medical evacuation, falling objects.

8. Emergency data replaced with verified local data: Police 104, Fire/Civil Defense 115, Ambulance 122, Unified Hotline 911, Al-Zubair General Hospital (~45 min), site first aider Haider (+964 770 731 3604); the previous international number was removed.

9. Technical limits verified and inserted: crane wind speed limit 9.5 m/s (rows 9–10); manual lifting per OSHA standard limits — 23 kg (51 lb) single-person maximum recommended weight limit (row 23); Heat Stress Protocol activated for summer operations (row 19).

10. Typos corrected (spelling, “SS extantion”, “POTANTIAL”, “VOLATILES”→vectors, “Panzer”→vaccination, EN136 mislabeled → FFP3 EN149).

11. Step 3 PPE matrix references specific risk numbers instead of blanket “All”; ATEX and pressure-vessel PPE rows added.

12. Approval block updated (Site Manager Raed Al-Nidawi; EHS Manager Ahmed Mansour; Project Manager & EHS Director names left for signature); field sign-off expanded to 64 lines; AL-MIAL Company subcontractor sign-off table added.

13. Step 1 ticks updated: hot work (4), welding (5), explosive/ATEX areas (14) and pressure vessels (26) confirmed relevant to this scope.

14. This version supersedes the earlier draft (“KAZ Project Risk Analysis 12 (Corrected).docx”). Remaining blank fields are intentionally for on-site completion: Project Manager & EHS Director names, AL-MIAL personnel, field team signatures, and briefing details in Step 5.

STEP 1 — RISK GROUPS (26) & RELATED WORK PERMITS

| No | Risk Group | Relevant Work Permit | Relevant to this JHA? (verified ticks) |
| --- | --- | --- | --- |
| 1 | Electric shock or exposure to electric arc | ELECTRICAL WORK PERMIT | X |
| 2 | Fall from height | WORK AT HEIGHT PERMIT | X |
| 3 | Falling object from height | WORK AT HEIGHT PERMIT | X |
| 4 | Hot work (oxy-LPG, oxy-acetylene, LPG, torch) | HOT WORK PERMIT | X (CONFIRMED IN SCOPE — thermal cutting) |
| 5 | Welding (electrode, aluminum) | HOT WORK PERMIT | X (CONFIRMED IN SCOPE — welding) |
| 6 | Ergonomic strain / manual handling | JHA | X |
| 7 | Hazardous waste | MOTAT Records | X |
| 8 | Use of mobile electrical panel and extension cable | ELECTRICAL WORK PERMIT | X |
| 9 | Use of crane, hoist, forklift, compressor, personal carrier, etc. | CRANE WORK PERMIT, LIFTING PLAN | X |
| 10 | Use of construction machinery (excavator, truck) | EXCAVATION WORK PERMIT | X |
| 11 | Angle grinder use | JHA | X |
| 12 | Use of chemical substances (ethyl alcohol, acid, base, epoxy, etc.) | JHA | X |
| 13 | Waste generation due to activity (cable, metal, paper, hydrocarbon, etc.) | MOTAT Records | X |
| 14 | Explosive areas | JHA + EXPLOSION RISK ASSESSMENT | X (CONFIRMED IN SCOPE — ATEX zones) |
| 15 | Exposure to dust, vapor, gas, welding fumes, chemical & biological agents | JHA | X |
| 16 | Moving machine parts or work equipment (entrapment, impact, etc.) | JHA | X |
| 17 | Slip and trip hazards on the ground | JHA | X |
| 18 | Contact with extremely cold or hot surfaces | JHA | X (added — turbine/piping during commissioning) |
| 19 | Working near energized open busbars and conductors in low-voltage systems | ELECTRICAL WORK PERMIT | X |
| 20 | Working in high-voltage system (≥1000 V) | ELECTRICAL WORK PERMIT, EKAD | X |
| 21 | Environmental factors, working in extremely hot & cold climate | JHA | X (added — Basra summer up to ~50°C; Heat Stress Protocol activated) |
| 22 | Hand tool use (hammer, cutting tools, etc.) | JHA | X |
| 23 | Use of scaffolding, ladder and platform | WORK AT HEIGHT PERMIT | X |
| 24 | Insufficient lighting and ventilation | CONFINED SPACE WORK PERMIT | X |
| 25 | Working in confined or restricted space | CONFINED SPACE WORK PERMIT | X |
| 26 | Use of pressure vessel | CONFINED SPACE WORK PERMIT + GAS-FREE CERT | X (CONFIRMED IN SCOPE) |

STEP 2 — RISK ASSESSMENT (corrected — Rev 1, verified data)

HAZARD / POTENTIAL RISK GUIDE — see Step 1 table for the verified tick marks.

Severity (S) — corrected scale:  1: No Injury   2: Minor Injury (First Aid)   3: Lost Time Injury   4: Major Injury / Permanent Disability (defined in Rev 1)   5: Death

Likelihood (L):  1: Very Unlikely   2: Unlikely   3: Likely   4: Very Likely   5: Certain

Risk Score bands (corrected):  1–7 = LOW (Acceptable, Monitor & Review)   8–12 = MEDIUM (Acceptable With Controls)   13–25 = HIGH (Unacceptable — EHS involvement required)

| No | Pathway of activity / hazard Precautions (corrected — Rev 1, verified data) |  |  |  |  |  | Post-control assessment (with controls in place) Permit (PTW) reference |  |  |  |  | Status (Rev 1) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | L | S | R | Rating |  | L | S | R | Rating |  |  |
| 1 | Pre-Work Compliance & Mobilization | 2 | 3 | 6 | Low | All personnel: valid WORK visa; medical certificate <12 months; vocational qualifications verified (crane, forklift, welder, scaffold erector, electrician, maintenance); site + SE EHS field induction completed with signed attendance; emergency plan understood (nearest hospital: Al-Zubair General Hospital, ~45 min; site first aider: Haider, +964 770 731 3604); SE and client risk assessments read; PPE issued per Step 3; working hours: max 11 h day / 7.5 h night, 1 rest day per 7 days, overtime ≤270 h/year; keep passport + local cash for contingencies. | 1 | 3 | 3 | Low | Checklist (not a PTW) | Corrected (L 4→2; also a mandatory checklist) |
| 2 | General Site Work | 3 | 3 | 9 | Medium | Complete LMRA before each task; work permits issued by SIEMENS ENERGY exclusively (verified PTW authority); notify plant operators (BGC/MOE) of any work affecting live areas; report observed risks to the SE client representative and request action; escalate to the Site Manager (Raed Al-Nidawi) if no action is taken. | 2 | 3 | 6 | Low | PTW per task (SE-issued) + LMRA | Corrected (PTW authority verified) |
| 3 | Driving & Transport to Site | 3 | 4 | 12 | Medium | Valid driver’s license for the vehicle type + medical fitness; journey planning (distance, road conditions, weather); obey traffic rules and speed limits; seat belt at all times; no mobile phone (incl. hands-free); no driving fatigued — break every 2 h; loads within weight limits and secured; daily vehicle inspection; no night travel without approval; tires suitable for Basrah conditions (summer heat / monsoon). | 2 | 3 | 6 | Low | N/A | Corrected (S 3→4: fatal road-accident potential in Iraq) |
| 4 | Unrestricted / Unbarricaded Area | 3 | 3 | 9 | Medium | Barricade the work area where possible; keep personnel who are not required out of the hazardous area; signage; trained and qualified personnel only. | 2 | 3 | 6 | Low | N/A | Corrected (old row 16) |
| 5 | Unauthorized Persons / Other Subcontractors in Work Area | 3 | 3 | 9 | Medium | Access control (ID badges); induction for every visitor/subcontractor; daily coordination meeting; demarcate zones; inform other subcontractors (incl. AL-MIAL) of cross-activity risks. | 2 | 3 | 6 | Low | Access / induction records | Corrected (old row 20) |
| 6 | Working at Height — Fall from Height | 2 | 5 | 10 | Medium | Work at height permit (SE-issued); scaffolding/working platform inspected and approved (tagged) before access; EN 361 full-body harness with proper anchor point; guardrails where possible; rescue plan for a suspended person. | 1 | 3 | 3 | Low | WORK AT HEIGHT PERMIT | Corrected (old rows 11+12 merged — duplicate removed; S 5→3 justified: harness converts a fatal fall to a survivable one) |
| 7 | Falling Object from Height | 3 | 4 | 12 | Medium | Tool lanyards; toe boards on platforms; exclusion zone below work; materials stacked and secured; signage; no work over occupied areas without protection. | 2 | 3 | 6 | Low | WORK AT HEIGHT PERMIT | NEW (risk group 3 ticked but had no row in Rev 0) |
| 8 | Slips, Trips & Falls on Same Level | 3 | 2 | 6 | Low | Cable ramps / cables routed outside the hazard zone; remove unneeded materials and tools; keep traffic routes clear; housekeeping; check floor for deformation, lubrication or gaps; non-slip footwear. | 2 | 2 | 4 | Low | N/A | Corrected (old row 13; S 3→2) |
| 9 | Lifting Operations (crane, hoist, forklift) | 3 | 4 | 12 | Medium | Crane Work Permit + Lifting Plan (SE-issued); certified operator + rigger + banksman; SWL respected (never exceed); slings/chains visually inspected with valid tag; exclusion zone under load — never stand under a load; spotter; WEATHER LIMIT: crane operations suspended above 9.5 m/s wind (verified); first-aid kit + extinguisher in vehicles. | 2 | 4 | 8 | Medium | CRANE WORK PERMIT + LIFTING PLAN | Corrected (old row 7 split: title now matches precautions; wind limit 9.5 m/s verified; residual stays MEDIUM) |
| 10 | Critical / Heavy Lifts (turbine module, generator, transformer) | 2 | 5 | 10 | Medium | Separate CRITICAL LIFT PLAN: critical-lift list and detailed specifications as per the approved Lifting Plan (verified scope); lift engineer appointed; load test; crane capacity and ground bearing verified; lifting director; dedicated exclusion zone; SE hold point before each critical lift; 9.5 m/s wind limit applies to all lifts. | 1 | 4 | 4 | Low | LIFTING PLAN (critical) — SE approval | NEW (specs per approved Lifting Plan) |
| 11 | Earthworks & Excavation | 3 | 4 | 12 | Medium | Excavation Permit (SE-issued); UTILITY LOCATE / SCAN before any digging — no excavation over underground services (cables, gas/steam lines) without a scan; shoring or sloping above 1.2 m depth; spoil kept off the edge; observer for equipment maneuvering; equipment licenses, driver documents + on-the-job training. | 2 | 3 | 6 | Low | EXCAVATION WORK PERMIT | Corrected (old row 22 — “Landscaping” removed; utility locate added: key gap in a live station) |
| 12 | Working in Confined Spaces (incl. entry/exit) | 2 | 5 | 10 | Medium | Confined Space Permit (SE-issued); atmospheric test (O2, LEL, H2S, CO) before entry AND continuous monitoring; stand-by attendant at the opening with constant communication; rescue equipment (tripod/harness) at the entry point; no lone working (min. 2 persons); gas-free certificate for tanks/bays; SELV/PELV electrical equipment only; access & egress clearly defined; emergency exit kept clear; housekeeping inside. Pressure vessels additionally per row 34. | 1 | 4 | 4 | Low | CONFINED SPACE WORK PERMIT | Corrected (old rows 9+14+15 merged; copied scaffolding text replaced) |
| 13 | Electrical Work — High Voltage (≥1000 V) | 3 | 5 | 15 | High | Precautions implemented by the executing subcontractor (AL-MIAL) under Siemens Energy direction — SE issues the Electrical Work Permit (sole PTW authority, verified); isolation coordination with plant operators (BGC/MOE) for live systems; 5 safety rules: isolate, lock out / tag out, verify that equipment cannot be re-energized, ground and short-circuit, maintain isolation from adjacent energized elements; only electrically trained and certified personnel; insulated tools; arc-rated PPE; rescue plan. | 1 | 4 | 4 | Low | ELECTRICAL WORK PERMIT + EKAD (SE-issued) | Corrected (responsibility corrected; S4 was undefined — now 5=Death; residual S kept at 4: isolation does not remove all residual arc/flash potential) |
| 14 | Working Near Energized Points (LV/HV busbars & conductors) | 3 | 5 | 15 | High | Live-area map agreed with plant operators (BGC/MOE) and SE; barricades + signage restricting the energized zone; safety distance calculated BEFORE work; energy shutdown requested where possible (then the 5 rules apply); otherwise Energized Work Permit (SE-issued); employees trained on energized points; no raising of held materials overhead. | 2 | 4 | 8 | Medium | ELECTRICAL WORK PERMIT (SE-issued) | Corrected (old row 23; residual stays MEDIUM — live-plant proximity cannot be reduced to Low without verified isolation) |
| 15 | Fire / Explosion (incl. oil storage & gas areas) | 2 | 5 | 10 | Medium | Hot Work Permit (SE-issued); remove combustible loads; fire watch assigned; appropriate extinguishing agents on site (CO2/D-class); gas cylinders ≥3 m apart or fire-resistant partition; hoses disconnected from supply when work interrupted; NO SMOKING in oil storage area; LEL monitoring in gas areas. | 1 | 4 | 4 | Low | HOT WORK PERMIT | Corrected (old row 18; S raised — gas/fuel-plant potential is fatal) |
| 16 | Natural Gas System Operations / Commissioning | 2 | 5 | 10 | Medium | CONFIRMED IN SCOPE (verified): gas-free certificate before work; continuous LEL monitoring (fixed + portable detectors tested); Hot Work Permit (SE-issued) + fire watch; mechanical and electrical isolation verified; procedure per OEM; qualified personnel only; gas pipeline integrity checks before energization. | 1 | 4 | 4 | Low | HOT WORK PERMIT + GAS-FREE CERT (SE-issued) | NEW (scope verified in Rev 1) |
| 17 | Work in a Live Operating Plant (interface with operations) | 3 | 5 | 15 | High | Joint JHA with plant operators (BGC & MOE) under SE coordination; live-area map updated and displayed; permanent barricades around live parts; agreed outage/blackout windows; single PTW authority: SIEMENS ENERGY (verified); daily interface meeting with BGC/MOE; no work inside the live zone without an SE-issued permit. | 2 | 4 | 8 | Medium | SE-issued PTW per task | NEW (residual permanently MEDIUM — inherent to an operating station) |
| 18 | Hot Surfaces (turbine, piping, steam during commissioning) | 3 | 4 | 12 | Medium | Surface temperature check before work; “HOT SURFACE” signage; temporary insulation; exclusion zone; heat PPE (EN 407); no work near surfaces >60 °C without treatment; gas-free before touching pipework. | 2 | 3 | 6 | Low | N/A | NEW (risk group 18 added in Rev 0) |
| 19 | Heat Stress (extreme climate — Basra) | 4 | 4 | 16 | High | HEAT STRESS PROTOCOL — ACTIVATED FOR SUMMER OPERATIONS (verified): work/rest cycle per protocol (45/15 min); mandatory hydration points; shaded/air-conditioned rest areas; acclimatization program for new arrivals; medical screening; schedule work in cool hours (night/early morning); monitor heat index; training on heat-illness symptoms; first-aid response for heat stroke (site first aider: Haider). | 2 | 3 | 6 | Low | N/A | NEW — protocol activated for summer operations (verified) |
| 20 | Noise Exposure (turbine / compressor areas) | 3 | 3 | 9 | Medium | Noise survey + dosimetry; hearing protection (EN 352) in designated zones; signage; limit exposure time; periodic hearing tests. | 2 | 2 | 4 | Low | N/A | NEW |
| 21 | Dust / Fume Exposure (cutting, grinding, welding fumes, chemicals) | 2 | 3 | 6 | Low | Wet cutting where possible; local exhaust ventilation; FFP3 respirator (EN 149 — corrected: template mislabeled EN 136); periodic air monitoring. | 1 | 2 | 2 | Low | N/A | NEW (risk group 15 ticked, no row existed in Rev 0) |
| 22 | Moving Machine Parts & Equipment (entrapment, impact) | 3 | 3 | 9 | Medium | Lock out machinery before maintenance; guards in place; no reaching into moving parts; trained personnel only; exclusion during operation. | 2 | 2 | 4 | Low | LOTO | NEW (risk group 16 ticked, no row existed in Rev 0) |
| 23 | Ergonomic Strain / Manual Handling | 3 | 2 | 6 | Low | Manual lifting per OSHA standard limits (verified): single-person lift maximum 23 kg (51 lb) — OSHA/NIOSH maximum recommended weight limit; team lift or mechanical aid required above that; lifting-technique training; task rotation. | 2 | 2 | 4 | Low | N/A | NEW (manual-lifting limit verified: OSHA standard) |
| 24 | Use of Chemical Substances | 2 | 3 | 6 | Low | SDS available on site for every chemical; labeled, segregated storage; use per SDS; chemical-specific gloves; spill kit at point of use. | 1 | 2 | 2 | Low | N/A | NEW (risk group 12 ticked, no row existed in Rev 0) |
| 25 | Oil / Hazardous Material Spill (turbine oil, hydraulic oil, chemicals) | 2 | 3 | 6 | Low | Spill kits at turbine-oil and hydraulic points; containment bunds; trained spill response; report to SE EHS (Ahmed Mansour) and BGC/MOE site EHS; SDS on site. | 1 | 2 | 2 | Low | N/A | NEW |
| 26 | Inadequate / Missing PPE (re-framed hazard) | 2 | 3 | 6 | Low | Hazard re-framed: PPE is a CONTROL; the hazard is non-use or damage. Minimum set: helmet EN 397 (chin strap at height), work shoes EN 345 S3, glasses EN 166, gloves EN 388, FFP3, high-visibility; task-specific: EN 361 harness (heights), arc clothing + electrical gloves (electrical), EN 407 (heat). Monthly inspection with records; issue by notification & receipt; replace on demand. | 1 | 3 | 3 | Low | PPE assignment form | Corrected (old row 8 re-framed) |
| 27 | Hand / Power Tools & Measuring Equipment | 3 | 3 | 9 | Medium | Tools appropriate to the task; visual inspection before use; guards fitted; safety devices never bypassed; low-vibration tools or scheduled breaks; tools secured against slipping; adjacent areas shielded from flying particles; hydraulic/pneumatic lines safely routed with whip checks; SDS followed for hydraulic fluids; trained personnel only. | 2 | 2 | 4 | Low | N/A | Corrected (old row 10 — duplicate sentences removed) |
| 28 | Waste Management | 3 | 2 | 6 | Low | Waste sorted by group (metal, cable, wood, paper, hydrocarbon); disposed in the designated waste area; MOTAT records; licensed disposal; no on-site burning. | 1 | 2 | 2 | Low | MOTAT Records | Corrected (old row 19 — S 3→2) |
| 29 | Fire Evacuation Awareness | 2 | 5 | 10 | Medium | Instructions communicated per the SE/BGC emergency procedure; evacuation routes and assembly points signed; MONTHLY evacuation drill (recorded); trained fire team; first-aid team trained (site first aider: Haider). | 1 | 4 | 4 | Low | N/A | Corrected (old row 17; S raised — evacuation failure in a fuel/gas plant is fatal) |
| 30 | Emergency Response / Evacuation Failure | 2 | 5 | 10 | Medium | Emergency Action Plan aligned with SE, BGC & MOE and communicated to all employees; response teams identified and trained (first aid, fire, search & rescue, evacuation) with recorded training; verified local emergency numbers posted visibly and on the back of every ID card (Police 104 / Fire 115 / Ambulance 122 / Unified 911 / first aider Haider +964 770 731 3604); first-aid & emergency kits content defined by the EHS specialist and technical authorities. | 1 | 4 | 4 | Low | N/A | Corrected (old row 24 re-framed; local numbers inserted) |
| 31 | Medical Evacuation / Delayed First Aid | 2 | 4 | 8 | Medium | Nearest hospital: AL-ZUBAIR GENERAL HOSPITAL (~45 min travel time — verified); site first aider on duty: HAIDER (+964 770 731 3604 — verified); dedicated transport vehicle; first-aid kits in all vehicles; trained first-aiders on site; medevac plan agreed with SE, BGC/MOE; the 45-min response window is the governing factor for first-aid readiness. | 1 | 3 | 3 | Low | N/A | NEW (hospital & first aider verified in Rev 1) |
| 32 | Security (theft, civil disturbance, travel risk — Iraq/Basra) | 3 | 4 | 12 | Medium | Security plan per SE site security requirements at the BGC/MOE-operated station: site access control & perimeter; patrols; safe room; redundant communications (satellite/backup); travel control and escort; insurance; regional situation monitoring. | 2 | 4 | 8 | Medium | N/A | NEW (residual permanently MEDIUM — regional risk) |
| 33 | Wild Animal Bites / Vector-Borne Disease | 2 | 4 | 8 | Medium | Routine vaccination completed before travel + regional immunizations if required; vector control (screens, nets, still-water removal, chemical control by experts); behavioral training (food disposal, clothing, repellents); first-aid training (wash bite with soap & cold water 5 min, apply pressure, seek help immediately — ambulance 122); hospital with snake antivenom: Al-Zubair General Hospital (~45 min). | 1 | 3 | 3 | Low | N/A | Corrected (old row 21 — “Panzer status”→vaccination, “volatiles”→vectors, copied driving sentence removed; residual now actually improves 8→3) |
| 34 | Pressure Vessel Operations (inspection, testing, vessel work) | 2 | 5 | 10 | Medium | CONFIRMED IN SCOPE (verified): pressure vessels treated as confined spaces — Confined Space Permit (SE-issued) + gas-free certificate; depressurize, isolate and blind/lock out per the 5 safety rules; atmospheric testing before entry; qualified inspectors for internal inspection; hydrostatic/pneumatic test procedure with barricaded test zone and controlled release; no internal work without SE approval. | 1 | 4 | 4 | Low | CONFINED SPACE WORK PERMIT + GAS-FREE CERT (SE-issued) | NEW — confirmed in scope (Rev 1) |
| 35 | Work Within/Near Hazardous & Explosive Areas (ATEX) | 2 | 5 | 10 | Medium | CONFIRMED IN SCOPE (verified): area classification (Zone 0/1/2) per gas hazard assessment; only Ex-rated electrical equipment and instruments suitable to the zone; intrinsically safe communications and test equipment; non-sparking tools; continuous LEL monitoring; Hot Work Permit (SE-issued) with gas-free; explosion-risk assessment for each hot-work job; ATEX training for all assigned personnel; no unapproved equipment in hazardous zones. | 1 | 4 | 4 | Low | HOT WORK PERMIT + EXPLOSION RISK ASSESSMENT (SE-issued) | NEW — confirmed in scope (Rev 1) |
| 36 | STOP Authority / Incident Management | — | — | — | n/a | REMOVED FROM THE RISK MATRIX (old rows 4 & 5): these are EHS management processes, not hazards — they cannot be scored L×S. Tracked as EHS program KPIs: stop-usage statistics, incident & near-miss reporting rate, investigation closure, lessons learned. Incident reporting: immediate, no matter how minor; everyone supports the investigation and corrective/preventive actions. | — | — | — | n/a | N/A | Removed — moved to EHS program |

Row mapping (Rev 0 → Rev 1):  11 & 12 (duplicate) → 6  |  14 & 15 (duplicate + copied text) → 12  |  4 & 5 (management processes) → 36 (unscored)  |  7 (mismatched) → 9  |  16 → 4  |  17 → 29  |  18 → 15  |  19 → 28  |  20 → 5  |  21 → 33  |  22 → 11  |  23 → 14  |  24 → 30  |  8 → 26  |  9 → 12  |  10 → 27  |  1 → 1  |  2 → 2  |  3 → 3  |  6 → 13.   New rows in Rev 1: 7, 10, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 31, 32, 34, 35.

STEP 3 — PPE & EQUIPMENT (references risk numbers — ATEX & pressure-vessel rows added)

| Work category (risk refs.) | LOTO | Helmet EN 397 | Ear plugs EN 352 | Safety shoes EN 345 S3 | Mech. gloves EN 388 | Heat gloves EN 407 | Protective clothing | Eyewear EN 166 | Face shield | Harness EN 361 | Arc clothing | Electrical gloves | FFP3 (EN 149) | Hi-vis | Fire ext. | Other |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| All work (baseline) | — | All | — | All | — | — | All | All | — | — | — | — | — | All | — | — |
| Electrical work (13, 14) | All | All | — | All | — | — | All | All | — | — | All | All | — | All | — | Insulated tools |
| Working at height (6, 7) | — | All (chin strap) | — | All | All | — | All | All | — | All | — | — | — | All | — | — |
| Confined space (12, 34) | — | All | — | All | All | — | All | All | — | All | — | — | FFP3 | All | — | Gas detector, tripod |
| Hot work / gas / ATEX (15, 16, 35) | — | All | — | All | EN 407 | EN 407 | All | All | All | — | — | — | FFP3 | All | On site | LEL meter, Ex-rated & non-sparking tools |
| Hot surfaces / commissioning (18) | — | All | — | All | EN 407 | EN 407 | All | All | All | — | — | — | FFP3 | All | On site | — |
| Pressure vessel (34) | All | All | — | All | EN 388 | — | All | All | All | — | — | — | FFP3 | All | On site | Gas-free cert, pressure-test barricade |
| ATEX zone (35) | All | All | — | Anti-static shoes | EN 388 | — | All | All | All | — | — | — | FFP3 | All | On site | Ex-rated & intrinsically safe equipment |

SUBCONTRACTOR PERSONNEL — AL-MIAL COMPANY (sign-off)

All AL-MIAL personnel assigned to the KAZPP scope must complete the site + SE EHS field induction BEFORE sign-off. This sign-off confirms assignment to this Safety and Scope of Work Document.

| Name | Position | Signature |
| --- | --- | --- |

STEP 4 — APPROVAL (sign-off block — 4 slots)

| Site Manager | Project Manager | EHS Manager | EHS Director | Result |
| --- | --- | --- | --- | --- |
| Name: Raed Al-Nidawi Date: ____________ Signature: ____________ Phone: ____________ | Name: (to be completed) Date: ____________ Signature: ____________ Phone: ____________ | Name: Ahmed Mansour Date: ____________ Signature: ____________ Phone: ____________ | Name: (to be completed) Date: ____________ Signature: ____________ Phone: ____________ | SUITABLE / NOT SUITABLE All four signatures are required before work authorization. Note: EHS approval (EHS Manager + EHS Director) is independent of the field execution team. |

NOTE: Project Manager and EHS Director names are intentionally left blank for completion at issue. Key SE site personnel for this project: Site Manager — Raed Al-Nidawi; EHS Manager — Ahmed Mansour (verified).

STEP 5 — COMMUNICATION TO EMPLOYEES & FIELD TEAM SIGN-OFF (64 lines — must be completed BEFORE work starts)

| Trainer / Sign | Training Area | Training Date |
| --- | --- | --- |
| (to be completed at briefing) | (to be completed at briefing) | (to be completed at briefing) |

| No | Name & Surname | Signature | No | Name & Surname | Signature |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  | 33 |  |  |
| 2 |  |  | 34 |  |  |
| 3 |  |  | 35 |  |  |
| 4 |  |  | 36 |  |  |
| 5 |  |  | 37 |  |  |
| 6 |  |  | 38 |  |  |
| 7 |  |  | 39 |  |  |
| 8 |  |  | 40 |  |  |
| 9 |  |  | 41 |  |  |
| 10 |  |  | 42 |  |  |
| 11 |  |  | 43 |  |  |
| 12 |  |  | 44 |  |  |
| 13 |  |  | 45 |  |  |
| 14 |  |  | 46 |  |  |
| 15 |  |  | 47 |  |  |
| 16 |  |  | 48 |  |  |
| 17 |  |  | 49 |  |  |
| 18 |  |  | 50 |  |  |
| 19 |  |  | 51 |  |  |
| 20 |  |  | 52 |  |  |
| 21 |  |  | 53 |  |  |
| 22 |  |  | 54 |  |  |
| 23 |  |  | 55 |  |  |
| 24 |  |  | 56 |  |  |
| 25 |  |  | 57 |  |  |
| 26 |  |  | 58 |  |  |
| 27 |  |  | 59 |  |  |
| 28 |  |  | 60 |  |  |
| 29 |  |  | 61 |  |  |
| 30 |  |  | 62 |  |  |
| 31 |  |  | 63 |  |  |
| 32 |  |  | 64 |  |  |

Declaration: “I guarantee that I will follow the rules mentioned in the precautions part of the risk assessment form, and also under negative conditions I will stop working in a safe way, then inform my project manager.”

ANNEX A — PROJECT-LEVEL RISKS (summary — full register: “KAZ PP Project Risk Register v1 (Corrected).xlsx”)

| ID | Project Risk | L | S | R | Rating | Owner | Mitigation (summary) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| P1 | Procurement / long-lead equipment delays (turbine parts, generator, transformers) | 3 | 5 | 15 | High | ■ TO BE ASSIGNED ■ | Early orders, on-site expediting, alternative sources, schedule buffer |
| P2 | Grid interconnection & synchronization (grid code, protection coordination, reverse power, connection permit) | 3 | 4 | 12 | Medium | ■ TO BE ASSIGNED ■ | Early coordination with grid operator / MOE, protection & sync studies, sync test plan |
| P3 | Interface with the operating plant: outage windows, production loss, operational liability (BGC/MOE) | 3 | 4 | 12 | Medium | ■ TO BE ASSIGNED ■ | Agreed outage windows, sequenced work packages, production-liability insurance, daily interface meeting |
| P4 | Hot commissioning (turbine start, run-up, load) deviations | 3 | 4 | 12 | Medium | ■ TO BE ASSIGNED ■ | OEM procedures, hold points, qualified test team, gas safety plan |
| P5 | Permitting & customs (equipment import via Basra port, environmental permits) | 3 | 3 | 9 | Medium | ■ TO BE ASSIGNED ■ | Early applications, local agent, document checklist before shipping |
| P6 | Security & geopolitical risk (Basra) | 3 | 4 | 12 | Medium | ■ TO BE ASSIGNED ■ | Site security plan, insurance, travel policy, regional monitoring |
| P7 | Currency (IQD) & payment terms | 3 | 3 | 9 | Medium | ■ TO BE ASSIGNED ■ | Contract currency clause, hedging, clear payment schedule |
| P8 | Subcontractor performance (AL-MIAL) / single-point dependency | 3 | 3 | 9 | Medium | ■ TO BE ASSIGNED ■ | Performance monitoring, KPIs, milestone payments, backup contractors |
| P9 | Extreme summer weather impacting schedule (Heat Stress Protocol active) | 4 | 3 | 12 | Medium | ■ TO BE ASSIGNED ■ | Schedule around work windows, night work, heat protocol (row 19) |
| P10 | Schedule delay / liquidated damages | 3 | 4 | 12 | Medium | ■ TO BE ASSIGNED ■ | Critical-path management, float monitoring, weekly early warning |

DOCUMENT STATUS: ISSUED FOR FORMAL REVIEW & APPROVAL — Doc No: 1, Rev: 1, 14.09.2026.  Prepared per the SE JHA methodology (SE-FO-0023).  Work may commence only after Steps 1–5 are completed, including this Step 5 sign-off by all assigned personnel (60+).  PTW authority: Siemens Energy exclusively.