PERMIT TO WORK (PTW) SYSTEM STANDARD OPERATING PROCEDURE

Project Name: KAZ Power Plant Upgrade Project (Basra, Iraq)

Document ID: KAZ-EHS-SOP-2026-003-  |  Revision:  (Updated Validity Periods & Electrical Categorization)

Author & Lead EHS: Ahmed Mansoor   (EHS Manager)  |  APPROVED SYSTEM MANUAL

| Document Parameter | System Specification & Control Standard |
| --- | --- |
| Project Title & Location | KAZ Power Plant Upgrade Project (Basra, Iraq) |
| Client / Beneficiary | Ministry of Electricity (MOE) & Basrah Gas Company (BGC) |
| Principal Contractor | Siemens Energy |
| Document Author | Ahmed Mansoor Hashim Kazem (EHS Manager,) |
| Governing Standards | Iraqi Occupational Safety Law, OSHA 29 CFR 1926/1910, NFPA 70E, Siemens Energy Global PTW Standard Framework |

## SECTION 1: PURPOSE & GENERAL SCOPE

The Permit to Work (PTW) system is a formal, written safety management process used to authorize specific high-risk activities on the KAZ Power Plant Upgrade Project. The system ensures that risks are systematically identified, proper control measures are verified on-site, and formal approval is documented before any work commences.

## SECTION 2: ROLES & RESPONSIBILITIES MATRIX

| Role Title | System Responsibilities & Authority |
| --- | --- |
| Permit Issuer (PI) | Authorized Siemens Energy Engineer/EHS Supervisor responsible for assessing site conditions, verifying safety precautions, conducting joint inspections, and signing to issue permits. |
| Permit Holder / Applicant (PH) | Competent Subcontractor Supervisor/Engineer requesting the permit. Responsible for briefing workers on Job Safety Analysis (JSA), maintaining site safety, and closing permits at shift end. |
| Authorized Electrical Person (AEP) / Isolation Officer | Certified Electrical/Mechanical Engineer responsible for conducting high/low voltage isolations, Commissioning testing, Arc Flash boundary assessments, grounding, LOTO application, and authorizing Electrical Cold/Hot Permits. |
| EHS Reviewer / Manager | Audits PTW implementation, reviews high-risk permits (e.g., Electrical Hot/Commissioning, Confined Space, Critical Lifting, LOTO), conducts random site checks, and halts work if permit conditions are breached. |
| Authorized Gas Tester (AGT) | Certified individual responsible for testing and recording atmospheric conditions (O2, LEL, H2S, CO) for Confined Space and Hot Work permits. |

## SECTION 3: PERMIT CATEGORIES, ELECTRICAL CLASSIFICATION & VALIDITY PERIODS

| Permit Category | Validity / Renewal | Scope of Activities Covered | Mandatory Prerequisites & Attachments | Key On-Site Control Measures |
| --- | --- | --- | --- | --- |
| 1. General Cold Work Permit | Weekly (Max 7 Days with Daily Endorsement) | General mechanical assembly/disassembly, piping installation, routine civil works, and non-hazardous maintenance not involving heat or live energy. | - Approved JSA / Method Statement. - Equipment pre-use inspection checklist. | - Standard PPE enforcement. - Housekeeping and path barricading. - Tool tethering and safe access routes. |
| 2. Electrical Cold Work Permit | Weekly (Max 7 Days with Daily Endorsement) | Non-energized electrical works, cable pulling, ladder tray installation, panel mounting, dead cable splicing, and general electrical installation activities (De-energized state). | - Approved JSA & Installation Method Statement. - Single-Line Diagram (SLD) / Layout Drawing. - Insulated Tool Inspection Checklist. | - Verification of completely de-energized system state. - Calibrated insulated hand tools (1000V rated). - Barricading around active installation zones. - Standard Electrical PPE (Safety Shoes, Leather Gloves). |
| 3. Electrical Hot Work & Commissioning Permit | Daily (Must be renewed every shift) | Energized electrical works, Commissioning activities, live testing/troubleshooting, switchgear energization, transformer testing, MCC energization, and high/low voltage (HV/LV) Commissioning tasks. | - Approved JSA & Commissioning Method Statement. - Single-Line Diagram (SLD) / Energization Plan. - Arc Flash Risk Assessment & Boundary Calculation. - AEP Authorization Certificate. | - Arc Flash PPE Category 2/4 (face shield, flame-resistant suit/hood). - Calibrated voltage detectors & insulated tools. - Dielectric insulating rubber mats installed at panel front. - AEP supervision required on-site during testing. - Barricading with Arc Flash warning signage around boundary. |
| 4. Energy Isolation (LOTO) Permit | Daily (Must be renewed every shift) | All mechanical, pneumatic, hydraulic, thermal, and electrical energy isolations associated with maintenance or Commissioning activities. | - Approved JSA & Isolation Plan. - P&ID / SLD Isolation Drawing. - LOTO Key Register & Isolation Certificate. | - Physical padlocks, hasps, and "DO NOT OPERATE" tags applied. - Zero Energy State verification test (voltage check, depressurization). - Lockbox key containment under AEP control. |
| 5. Hot Work Permit (Thermal / Open Flame) | Daily (Must be renewed every shift) | Welding, flame cutting, grinding, soldering, thermal spraying, or any activity producing sparks, open flames, or heat above 100°C. | - Approved JSA. - Fire Watch appointment form. - Gas Test certificate (if near fuel/chemical zones). | - Fire blanket containment & 10m combustible clearance. - Dedicated Fire Watch stationed during work + 30 min post-work. - Min. 2x 10kg Dry Chemical Powder / CO2 extinguishers at site. |
| 6. Excavation & Trenching Permit | Weekly (Max 7 Days with Daily Endorsement) | Manual or mechanical digging, trenching, piling, or ground penetration exceeding 30 cm depth. | - Underground Utility Clearance Map (signed by Electrical/Instrumentation). - Approved JSA & Soil Classification. | - Shoring, benching, or sloped walls for excavations > 1.2m. - Ladders positioned every 7.5m for emergency egress. - Spoil heaps set back at least 1.0m from trench edge. |
| 7. Lifting Permit (Mandatory Lifting Plan) | Daily (Must be renewed every shift) | ALL lifting operations using mobile cranes, tower cranes, overhead cranes, or heavy rigging gear without exception. | - APPROVED LIFTING PLAN (Mandatory for ALL lifts). - 3rd party crane & tackle certificates. - Operator & Rigger competency cards. | - Outriggers 100% extended on timber pads. - Barricaded exclusion zone around swing radius. - Taglines used for load control; no lifts in winds > 32 km/h. |
| 8. Work at Height Permit | Daily (Must be renewed every shift) | Any task performed at an elevated height of 1.8 meters or above where a fall hazard exists. | - Scaffold Green Inspection Tag. - Fall Protection Plan & JSA. | - 100% tie-off using double lanyard harnesses with shock absorbers attached to certified anchor points (> 22 kN). - Toe-boards and handrails installed on all working platforms. |
| 9. Confined Space Entry Permit | Daily (Must be renewed every shift) | Entry into tanks, pressure vessels, trenches > 1.2m deep, underground ducts, or areas with restricted entry/exit and potential hazardous atmospheres. | - Approved JSA & Emergency Rescue Plan. - AGT Gas Test Log (O2, LEL, H2S, CO). - Electrical & Energy Isolation (LOTO) Certificate. | - Continuous mechanical ventilation. - Stationed Standby Entrant/Attendant at entry point with logbook. - Full-body harness connected to tripod rescue winch. |

## SECTION 4: PERMIT VALIDITY & RENEWAL POLICY SUMMARY

SUMMARY OF PERMIT VALIDITY RULES:

- WEEKLY PERMITS (Valid up to 7 Days with Daily Shift Check/Endorsement):

  - General Cold Work Permit

  - Electrical Cold Work Permit (Installation / Non-Energized)

  - Excavation & Trenching Permit

- DAILY PERMITS (Must be Issued and Re-evaluated Daily / Every Shift):

  - Electrical Hot Work & Commissioning Permit (Energized / Testing)

  - Energy Isolation (LOTO) Permit

  - Hot Work Permit (Thermal / Welding / Cutting)

  - Lifting Permit (Cranes & Heavy Rigging)

  - Work at Height Permit (≥ 1.8m)

  - Confined Space Entry Permit

## SECTION 5: PERMIT LIFECYCLE & WORKFLOW PROCEDURES

THREE-STEP PERMIT MANAGEMENT WORKFLOW:

- Application & Submission (T-24 Hours): The Permit Holder submits the PTW request along with JSA, Method Statement, and required attachments (e.g., LOTO Isolation Certificate, Mandatory Lifting Plan, Gas Test Log) to EHS at least 24 hours prior to work execution.

- Joint Field Verification & Issuance: The Permit Issuer and Permit Holder conduct a physical walk-through of the work site to verify all controls (including zero-energy state verification). Upon satisfaction, both sign the PTW. The Original Permit is displayed at the work location inside a weatherproof plastic sleeve.

- Shift Completion & Closure: At shift end (or task completion), the site is cleaned, tools removed, de-isolation executed if authorized, and the Permit Holder & Issuer sign off the permit closure section. Closed permits are archived at the EHS Office. Daily permits expire at the end of the shift and must be re-issued for subsequent shifts.

## SECTION 6: EMERGENCY SUSPENSION & BREACH PENALTIES

MANDATORY PERMIT SUSPENSION TRIGGERS:

- Emergency site alarm activation or gas release incident.

- Unannounced change in weather conditions (e.g., wind speed > 32 km/h during lifting, heavy rain, dust storm).

- Violation of permit conditions, missing PPE (e.g., Arc Flash suits or LOTO padlocks), or unapproved scope changes (Immediate PTW Revocation + Stop Work Notice).

## SECTION 7: SIGN-OFF & APPROVAL MATRIX

| Prepared By | Reviewed By | Approved By |
| --- | --- | --- |
| Name: Ahmed Mansoor Hashim Kazem Role: EHS Manager (Siemens Energy) Status: Date: 06 / 09 / 2026 | Name: Dogukan Arandi Role: EHS Director Company: Siemens Energy Status: Date: ___/___/2026 | Name: Onur Ozvatan Role: Project Director Company: Siemens Energy / MOE / BGC Status: Approved Date: ___/___/2026 |