KAZ PTW (Permit to Work) Procedure Review Report

The procedure is generally well developed and covers the main high-risk work activities. However, the following points should be clarified before final approval.

1. PTW Authority and Approval Process

It should be clarified whether the PTW system will be controlled by MOE/BGC or Siemens Energy.

Permit Issuer, Area Authority and Isolation Authority roles should be clearly defined.

If the client PTW system will be used, the procedure should be aligned accordingly.

2. Separation of EHS and Operational Authority

EHS should act as reviewer and auditor.

Technical permit approval authority should remain with the responsible operational or area authority.

3. PTW and LOTO Management

PTW validity and LOTO validity should be managed separately.

Handover and isolation control requirements during shift changes should be defined.

4. Lifting Operations

The requirement for a detailed lifting plan for all lifting activities should be reviewed.

Critical lifts and routine lifts should be clearly differentiated.

5. Confined Space Definition

Excavations deeper than 1.2 m should not automatically be classified as confined spaces.

Confined space classification should be based on risk assessment and actual conditions.

6. Reference for Technical Limits

Numerical limits such as wind speed, working at height criteria and excavation depth limits should reference applicable standards or client requirements.

Applicable Siemens Energy standards, client requirements or legal regulations should be referenced.

7. Document Status and Approval Matrix

The “Approved System Manual” status should be reviewed if the document has not yet completed the approval process.

Roles, titles and approval authorities should be aligned with the actual project organization.

Conclusion

The PTW procedure is generally acceptable. However, the most important item requiring clarification is who holds the PTW authority and approval responsibility on site. Once this is clarified and the above comments are addressed, the procedure should be suitable for approval.