## 01 Cover & Methodology
SE GT SU Kaz Power Plant Upgrade Project Risk Analysis
Job-based hazard analysis is performed in A, B, C, Small projects and, by decision of EHS managers, in all projects. Job-based hazard analysis and the work permit consist of 5 steps: Steps 1, 2, 3, 4 and 5.
Step 1
EXPLANATION: The existing general potential risks and hazards in the work area are defined. The relevant risk is ticked. 26 risk groups were defined.
Risk Groups | Relevant Work Permits | Work permits related to the risk groups in Step 3
1- Electric shock or exposure to electric arc |  | 1 | ELECTRICAL WORK PERMIT
2- Fall from height |  | 2 | WORKING AT HEIGHT PERMIT
3- Falling object from height |  | 3 | WORKING AT HEIGHT PERMIT
4- Hot work (oxy-LPG, oxy-acetylene, LPG, torch) |  | 4 | HOT WORK PERMIT
5- Welding (electrode, aluminum) |  | 5 | HOT WORK PERMIT
6- Ergonomic strain / manual handling |  | 6 | JHA
7- Hazardous waste |  | 7 | MOTAT Records
8- Use of mobile electrical panel and extension cable |  | 8 | ELECTRICAL WORK PERMIT
9- Use of crane, hoist, forklift, compressor, personal carrier, etc. |  | 9 | CRANE WORK PERMIT, LIFTING PLAN
10- Use of construction machinery (excavator, truck) |  | 10 | EXCAVATION WORK PERMIT
11- Angle grinder use |  | 11 | JHA
12- Use of chemical substances (ethyl alcohol, acid, base, epoxy, etc.) |  | 12 | JHA
13- Waste generation due to activity (cable, metal, paper, hydrocarbon, etc.) |  | 13 | MOTAT Records
14- Explosive areas |  | 14 | JHA
15- Exposure to dust, vapor, gas, welding fumes, chemical and biological agents |  | 15 | JHA
16- Moving machine parts or work equipment (entrapment, impact, etc.) |  | 16 | JHA
17- Slip and trip hazards on the ground |  | 17 | JHA
18- Contact with extremely cold or hot surfaces |  | 18 | JHA
19- Working near energized open busbars and conductors in low-voltage systems |  | 19 | ELECTRICAL WORK PERMIT
20- Working in high-voltage system (≥1000 V) |  | 20 | ELECTRICAL WORK PERMIT, EKAD
21- Environmental factors, working in extremely hot & cold climate |  | 21 | JHA
22- Hand tool use (hammer, cutting tools, etc.) |  | 22 | JHA
23- Use of scaffolding, ladder and platform |  | 23 | WORKING AT HEIGHT PERMIT
24- Insufficient lighting and ventilation |  | 24 | CONFINED SPACE WORK PERMIT
25- Working in confined or restricted space |  | 25 | CONFINED SPACE WORK PERMIT
26- Use of pressure vessel |  | 26 | CONFINED SPACE WORK PERMIT
Step 2
Existing work steps should be written one by one and work equipment to be used specifically for the job should be specified on a separate line for construction equipment and subjected to hazard assessment. Severity and likelihood are entered for each step. The severity/likelihood table uses a 5x5 matrix. According to the severity and likelihood result, the Risk score should be entered as low, medium and high. Control measures for each written step must be evaluated, and the risk score should decrease in line with the measures taken/to be taken.
Step 3
Relevant PPE is selected to protect against the risks mentioned in Step 2. Under each PPE in Step 3, the related risk number from Step 2 is referenced to confirm.
Step 4
This is the approval section of the job hazard analysis. The site manager/field supervisor and OHS specialist conduct the final review and mark the appropriate section. The OHS specialist informs the field supervisor/site manager as needed that work permits are required for the relevant work steps. If 'Not Suitable' is indicated, this hazard assessment must be redone. Work cannot start during this time.
Step 5
The approved job hazard analysis must be communicated to employees. In this section, the person performing or supervising the work conveys the content of Steps 2 and 3 to employees. Employees acknowledge by writing their name, surname and signature in the spaces provided to confirm they accept the items in Steps 2 and 3.
Work starts after Step 5 is completed.

## 02 JHA Header + Step 1
|  | Job Hazard Assesment (JHA) |  |  |  |  | Document No: | 1 |  |  | Date: 04.03.2026
[7 empty] | Subcontractor |  |  |  | Personnel Tot.:
Activity : Kaz Power Plant Upgrade Project (Constraction, instalation, Test of SS extantion) | [6 empty] | Used Vehicles : Manlift, Crane, Truck, Excavator |  |  | Used Equipments : Hand Tools, Power Tools, Lifting Equipments, Test Equipments
Location : Basrah Iraq
Work Area : Khur Alzubair Power Station
Team Member | Uğur Akbulut, Onur Özvatan, Abdurrahman Öğüt, Doğukan Arandı
NOTE: If after risk evaluation and with all the necessary controls in place; the risk rating (R) is HIGH, the EHS department are to be contacted for guidance on the task/process. | [9 empty] | POLICE | FIRE STATION | AMBULANCE
SIEMENS ENERGY EMERGENCY CONTACT NUMBER +90 533 625 9494 | [9 empty] | 112
STEP 1 / ADIM 1 | HAZARD / POTANTIAL RISK GUIDE
HAZARD / POTANTIAL RISK GUIDE | Contact with electric shock or arc electric / Elektrik çarpması veya elektrik arkına maruziyet |  | x | The use of electrical panel and elektrical cable / Seyyar elektrik panosu ve elektrik uzatması kullanımı | x | Contact with dust, steam, gas,welding smoke, biological & chemical substances / Toz, buhar, gaz, kaynak dumanına,kimyasal ve biyolojik maddelere maruziyet |  |  | Working with overtemp & extreme cold ,environmental factors / Çevre faktörleri, aşırı sıcak & soğuk iklim şartlarında çalışma
| Falling from height / Yüksekten düşme |  | x | The use of cranes, chain hoist, forklift, compressors, personel lift, etc. / Vinç, ceraskal, forklift, kompresör, kişisel taşıyıcı v.b. kullanımı | x | Moving part of the machines or work equipment / Hareketli makina parçaları veya iş ekipmanı (sıkışma, çarpma, v.b.) |  | x | The use of hand tools / El aletleri kullanımı (çekiç, kesici alet, v.b.) |  |  | x
| Piece falling from height / Yüksekten parça düşmesi |  | x | The use of construction equipment (scoop, truck) / İş makinası kullanımı (kepçe, kamyon) | X | Slipping points on the ground / Zeminde kayma takılma noktaları |  | x | The use of scaffolding, stairs, platform / İskele, merdiven ve platform kullanımı |  |  | x
| Termal cutting (oxy lpg, oxy acetylene,LPG, torch / Isıl işlem (oksi-lpg, oksi-asetilen, LPG, şaloma) |  |  | The use of spiral grinding engine / Spiral taş motoru kullanımı | X | Contact with extremely cold or hot surfaces / Aşırı soğuk veya sıcak yüzeylere temas |  |  | Inadequate lighting and ventilation / Yetersiz aydınlatma ve havalandırma |  |  | x
| Welding (Electrodes,aluminium,) / Kaynak yapılması (Elektrot,Aluminyum) |  |  | The use of chemical substances (ethyl alcohol, acid, base, epoxy etc.) / Kimsayal madde kullanımı (etil alkol, asit, baz, epoksi, vb) | x | Near working around low voltage conductives and energized opened bare / Alçak gerilim sisteminde enerjili açık bara ve iletkenlere yakın çalışma |  | X | Working with closed and circumscribed area / Kapalı ve sınırlandırılmış alanda çalışma |  |  | x
| Ergonomic strain / lifting heavy / Ergonomik zorlanma / ağır taşıma |  | x | Produced waste as a result of activity (cable,metal,paper,hydrocarbons.etc) / Faaliyet sonucu atık oluşumu (kablo, metal, kağıt, hidrokarbon , vb) | x | Working with high voltage ( ≥1000 V ) / Yüksek gerilim sisteminde ( ≥1000 V ) çalışma |  | X | The use of pressure vessel / Basınçlı kap kullanımı
| Hazardous Waste / Tehlikeli Atıklar |  | X | Explosive Area / Patlayıcı Alanlar |  | Others / Diğer Çalışmalar .......................................................................... .......................................................................... .......................................................................... .......................................................................... |  |  | Others / Diğer Çalışmalar .............................................................................................................................. .............................................................................................................................. .............................................................................................................................. .........................

## 03 Step 2 Risk Assessment
STEP 2 | THIS DOCUMENT IS RECORDED AND STORED BY THE DOING THE JOB
Persons Affected: (e.g.operators,maintenance,visitors,public etc): |  |  |  | Handling: For Siemens Energy internal and subcontractor use only. Review: If there is a change in working methods and conditions, the form must be renewed. |  |  |  | Likelihood 1 2 3 4 5 1 5
The Risk Assesment 1. Identify and record for each hazard/risk identified the appropriate rating for severity and likelihood without control. 2. Identify and record the control measures to be used then repeat the assessment with the controls in place. |  | Severity (S) 1:No Injury 2:Minor Injury 3:Lost time Injury 5:Death or Permanent Disability |  | Likelihood of harm (L) 1:Very Unlikely 2:Unlikely 3:Likely 4:Very Likely 5:Certain |  |  | Risk Score (R) = S x L 1 to 6 = Low Risk (L) (Acceptable, Monitor & Review) 8 to 12 = Medium Risk (M) (Acceptable With Controls) >12 = High Risk (H) Unacceptable
[9 empty] | 1 |  | 2 | 3 | 4 | 5
[8 empty] | 4 3 2 Severity | 2 |  | 4 | 6 | 8 | 10
[9 empty] | 3 |  | 6 | 9 | 12 | 15
[9 empty] | 4 |  | 8 | 12 | 16 | 20
[9 empty] | 5 |  | 10 | 15 | 20 | 25
No | Pathway of activity / |  | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions |  | Assessment / Değerlendirme High (H)
|  |  | Likelihood (L) | Severity (S) | Risk Score(R) |  |  | Likeliho od (L) |  | Severity (S) |  |  | Risk Score(R)
1 | BEFORE WORK |  | 4 | 3 | 12 | 1-Make sure you have a valid assembly visa before going to the country for work1- Ensure a valid work visa and valid employment documents are available before going to the country for work. 2-A competent person must be appointed for the specific task. For certain jobs (crane operator, forklift operator, welder, 2- Strict compliance to PTW system - the safety work permit and all pertinent documents shall be secured before work scaffold builder, electrician, mechanical maintenance man, etc.) the necessary vocational training and qualification documents commence. should be requested. Unauthorized personnel should not work outside of the job description.3- Customer safety induction training and SE EHS field induction training to be taken before starting work at the construction 3-Make sure that you have a health report approved by the doctor for the last year or valid in your country.site; the training attendance report must be signed by each employee. 4-Customer safety induction training and SE EHS field induction training should be taken before starting to work at the 4- Siemens Energy and the customer risk assessment must be properly read, understood and discussed with all personnel construction site. Learn the emergency management plan and actions from the customer. (Nearest hospital, timing, etc.)before starting work. 5-Siemens Energy and the customer risk assessment must be properly read and understood before starting work. In addition, 5- A competent person must be appointed for the specific task. For certain jobs (crane operator, forklift operator, welder, the training attendance report must be signed by each employee.scaffold builder, electrician, mechanical maintenance man, etc.) the necessary vocational training and qualification 6-Unexpected earthquake, fire, explosion, etc. Keep your passport and some local cash in case of need.documents should be requested. Unauthorized personnel should not work outside of the job description. 7-The project site has a lot of risks within the scope of the work area, personal protective equipment should be provided for 6- A health report approved by the doctor for the last year (or valid in the home country) must be available for all personnel. each employee.7- Minimum PPE to be provided and worn by each employee: Helmet EN 397 (chin-attached), work shoes EN 345 S3 with * High visible clothingankle protection, safety glasses EN 166, ear protection, protective work gloves EN 388, protective dust mask (FFP3), * Chin-attached helmetshigh-visibility clothing, disposable overalls, head lamp. * Head lamp8- All crew must be familiar with the emergency management plan and actions from the customer (nearest hospital, * Work shoes with ankle protectionresponse timing, muster points). *Ear protection9- Keep your passport and some local cash in case of unexpected events (earthquake, fire, explosion, etc.). *Safety glasses10- Daily working hours cannot exceed 11 hours during the day and 7.5 hours at night, excluding rest periods. * Protective work gloves11- Seven days of uninterrupted work cannot be done; one day of rest is obligatory within seven days. Annual overtime *Protective dust mask (FPP3)cannot exceed 270 hours. * Disposable overalls 12- Certified First Aider with valid certificates must be present at site; first aid kit to be stocked and accessible. 8-Daily working hours cannot exceed 11 hours during the day and 7.5 hours at night, excluding rest periods. 13- Emergency procedure to be followed. Stop Work Authority applies at all times. NO HSE - NO WORK. 9-Seven days of uninterrupted work cannot be done, one day of rest is obligatory within seven days. 10-The annual overtime period cannot exceed 270 hours. |  | 4 |  | 1 |  |  |  | 4
2 | GENERAL SITE WORK |  | 4 | 3 | 12 | 1- Fill the "LMRA" form before starting work and get the necessary work permit from the client.1- Fill the "LMRA" form before starting work and get the necessary work permit from the client; strict compliance to PTW requirements. 2- When you see the risks that may affect you at the project site, inform the customer and ask for action. 2- Conduct TBT at the start of each shift; the RA to be discussed daily with the workers. 3- When risks are observed, inform the customer immediately and ask for action; if no action is taken, notify the project manager. 3- Notify the project manager of the situation if the client does not take any action. 4- Minimum PPE at all times: Helmet EN 397, work shoes EN 345 S3, safety glasses EN 166, gloves EN 388, high-visibility vest. NO HSE - NO WORK. |  | 4 |  | 1 |  |  |  | 4

## 04 Step 2 cont (PDF p4)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
3 | DRIVING - TRANSPORT TO SITE | 3 | 3 | 9 | 1-Everyone must have a valid driver's license for the type of vehicle they drive and be medically fit to drive, in 1- Everyone must have a valid driver's license for the type of vehicle driven and be medically fit to drive, in accordance with local regulations.accordance with local regulations. 2-Everyone is expected to plan their journeys taking into account distance, road conditions, travel time and weather 2- Vehicle must be approved from third party and client; daily vehicle inspections by driver before departure. conditions.3- Trained personnel, certified operator only. 3-Everyone must obey all local traffic regulations and speed limits while driving.4- Obey all local traffic regulations and speed limits while driving. 4-No one should drive while under the influence of drugs or alcohol.5- Seatbelt compliance at all times. 5-Everyone should wear a seat belt at all times.6- Plan journeys taking into account distance, road conditions, travel time and weather conditions. 6-No one should use mobile phones or other devices that cause distraction while driving, including in hands-free 7- No one should drive while under the influence of drugs or alcohol. mode - this is unsafe and unacceptable.8- No one should use mobile phones or other devices that cause distraction while driving, including in hands-free 7-Eating, drinking, setting up a radio or GPS device, etc. It is expected to minimize the risk of distraction.mode - this is unsafe and unacceptable. Minimize distraction (eating, drinking, radio/GPS setting). 8-No one should drive when tired or suffering from fatigue.9- No one should drive when tired or suffering from fatigue; take adequate breaks at least every two hours. If you 9-Everyone should take adequate breaks to drive at least every two hours. If you feel tired, stop and rest.feel tired, stop and rest. 10-Anyone who orders and uses external personal transportation services and rents a vehicle must ensure that they 10- Ensure the loads carried are within the vehicle weight and load limits and are properly secured before meet this Zero Accident Culture behavior and the “Vehicle Safety” Principle.departure. 11-Everyone should ensure that the loads carried are within the vehicle weight and load limits, and that the loads 11- Be careful about the possibility of wild or domestic animals on the road. carried are properly secured before departure. 12- Use the vehicle considering weather conditions (rain, snow, fog, icing); tyres suitable for seasonal conditions. 12-While driving, you should be careful about the possibility of wild or domestic animals on the road.13- Road survey for obstacles and overhead structures; flagman or escort vehicle if required. 13-The vehicle should be used considering weather conditions such as rain, snow, fog, icing. 14- Vehicle must be equipped with fire extinguisher and first aid kit; certified first aider must be available. 14-Tires suitable for seasonal conditions should be used (such as winter tires in cold and rainy weather, summer 15- Emergency procedure to follow. Stop Work Authority applies. NO HSE - NO WORK. tires in hot weather) | 3 | 1 | 3
4 | GENERAL SITE WORKS (STOP) | 4 | 3 | 12 | 1-Everyone is empowered to apply Stop any time there is a potential risk of harm or non-compliance with Zero Harm 1- Everyone is empowered to apply STOP! any time there is a potential risk of harm or non-compliance with Zero Harm Behaviours, Essentials, local Zero Harm programs, or legal requirements.Behaviours, Essentials, local Zero Harm programs, or legal requirements. 2-Taking into consideration the severity of the circumstances, Stop! may be issued by anyone as follows:2- Taking into consideration the severity of the circumstances, STOP! may be issued by anyone as follows: *Immediate direct verbal Stop!, usually involving minor non-compliance, including unsafe acts or conditions that can be easily - Immediate direct verbal STOP!, usually involving minor non-compliance, including unsafe acts or conditions that can be corrected on the spot without delay. easily corrected on the spot without delay. *Immediate notification of Stop! to the responsible person in charge of the work activity or workplace condition for immediate - Immediate notification of STOP! to the responsible person in charge of the work activity or workplace condition for corrective action. immediate corrective action. 3-Everyone experiencing a Stop! notification from another individual is expected to receive it in a constructive way and as a 3- Everyone experiencing a STOP! notification from another individual is expected to receive it in a constructive way and as kind reminder of our Zero Harm Principle that “We Take Care of Each Other.”a kind reminder of the Zero Harm Principle "We Take Care of Each Other". 4-Everyone must respect the Stop!, and it shall remain in force until required corrective measures have been put in place. 4- Everyone must respect the STOP!, and it shall remain in force until the required corrective measures have been put in 5-When in doubt how to resolve a situation leading to a Stop!, everyone must consult their managers and verify the place. applicability and implementation of required measures. 5- When in doubt how to resolve a situation leading to a STOP!, everyone must consult their managers and verify the applicability and implementation of required measures. 6- NO HSE - NO WORK. Emergency procedure to follow. | 4 | 1 | 4
5 | INCIDENT MANAGEMENT | 4 | 3 | 12 | 1-Everyone needs to know the Siemens Energy definitions and procedures for reporting incidents and near misses.1- Everyone needs to know the Siemens Energy definitions and procedures for reporting incidents and near misses. 2-Everyone should ensure that any incident or near miss they are involved in or witnessed is reported to their manager or 2- Any incident or near miss that a person is involved in or witnesses must be reported to the manager or supervisor without supervisor without delay.delay. 3-Anyone who experiences an injury, no matter how minor, or who experiences sudden pain from a work activity should speak 3- Anyone who experiences an injury, no matter how minor, or sudden pain from a work activity must speak up without delay up without delay and report the situation to their manager or supervisor.and report the situation to the manager or supervisor. 4-Anyone who has been involved in or witnessed an incident or near miss will support the investigation process and contribute 4- Anyone involved in or witnessing an incident / near miss will support the investigation process and contribute to cause to cause analysis, lessons learned and closure of the incident.analysis, lessons learned and closure of the incident. 5-Everyone should be familiar with the corrective and preventive measures required following the investigation process and be 5- Everyone should be familiar with the corrective and preventive measures required following the investigation process and fully aware of any changes in procedures or risk assessments covering business activities.be fully aware of any changes in procedures or risk assessments covering business activities. 6-Everyone should support the implementation of corrective and preventive measures by proactively checking that everyone 6- Support the implementation of corrective and preventive measures by proactively checking that everyone you work with is they work with is fully aware of changes.fully aware of changes. 7- Daily TBT to reinforce incident reporting culture; emergency procedure to follow. | 4 | 1 | 4
6 | WORKING UNDER ELEVATED PHYSICAL | 3 | 3 | 9 | 1-Plan for adequate breaks1- All personnel to be familiar with correct handling / lifting / carrying techniques (lift using the legs and arms, not the back). 2-Avoid work that is too frequent or too long, requires extreme distances, or is done with insufficient rest time.2- Seek assistance when attempting to move heavy loads; use auxiliary equipment for lifting and transporting where possible. 3- Plan for adequate breaks; avoid work that is too frequent or too long, requires extreme distances, or is done with insufficient rest 3-Use auxiliary equipment for lifting and transporting. If it is not possible to use the equipment, get help from other employees. time. 4-Take into account the physiological state of the employee 4- Take into account the physiological state of the employee; assign only those personnel who are physically fit to perform the task. 5-The characteristics of the load such as size, weight, manageability, location of the center of gravity, external and/or internal 5- The characteristics of the load (size, weight, manageability, location of the center of gravity, external and/or internal hazards) characteristics shall be taken into account. shall be considered before handling. | 3 | 1 | 3

## 05 Step 2 cont (PDF p5)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
7 | WORKING AT HEIGHT | 5 | 3 | 15 | 1-Scaffolding installation/dismantling must be done by competent personnel, the necessary documents regarding scaffolding 1- Scaffolding installation / dismantling must be done by competent and authorized personnel; the necessary documents regarding suitability will be submitted by the customer to Siemens Energy before the work.scaffolding suitability will be submitted by the customer to Siemens Energy before the work. 2- Scaffolding should only be installed or replaced by a specialized company; all scaffolding to be inspected weekly by a trained 2-Personnel working on the scaffold must use the necessary PPE (full body protection seat belt, yoyo, lifeline, etc.) and qualified scaffolding inspector. 3-Materials and equipment should not be left on scaffolding, access platforms, etc. at the end of the work or during shift 3- Only access inspected and approved scaffolding - green label is suitable, red label is not suitable. ScaffTag to be displayed. change. The risk of objects falling should be eliminated. 4- Every employee should check the scaffolding to observe obvious deficiencies before going on the scaffolding. 4-Work should not be done on scaffolds where guardrails and barriers have not been installed. 5- Personnel working on the scaffold must use the necessary PPE: full body harness EN 361 with double lanyard (yoyo) and lifeline 5-Only access inspected and approved scaffolding. Scaffolds with green labels are suitable, those with red labels are not - 100% tie-off. suitable. 6- In the work to be done on the GT, the use of yoyos attached to the lifeline should be a priority. In cases where lifelines need to 6-Scaffolding should only be installed or replaced by a specialized company. be dismantled due to the requirements of the lifting operation, the yoyos should be connected to the ceiling crane, anchor points 7-All scaffolding should be inspected weekly by a trained and qualified scaffolding inspector. should be used, or the yoyos and the turbine should be anchored at appropriate points to be determined and seat belts should be 8-Every employee should check the scaffolding to observe obvious deficiencies before going on the scaffolding. used. 9-Each study should be evaluated on its own and collective protection measures should be given priority. In cases where 7- Materials and equipment should not be left on scaffolding, access platforms, etc. at the end of the work or during shift change; collective protection measures cannot be taken, precautions should be taken with personal protective equipment and the risk of objects falling should be eliminated. equipment. 8- Work should not be done on scaffolds where guardrails and barriers have not been installed; all openings and edges to be 10- In the work to be done on the GT, the use of yoyos attached to the lifeline should be a priority. In cases where lifelines closed. need to be dismantled due to the requirements of the lifting operation, the yoyos should be connected to the ceiling crane, 9- Each study should be evaluated on its own and collective protection measures should be given priority; where collective anchor points should be used, or the yoyos and the turbine should be anchored at appropriate points to be determined and protection measures cannot be taken, precautions should be taken with personal protective equipment and equipment. seat belts should be used.10- Minimum PPE for work at height: Helmet EN 397 with chin strap, full body harness EN 361 with double lanyard, work shoes EN 345 S3, safety glasses EN 166, gloves EN 388. 11- Conduct TBT before start of work; emergency procedure to follow; certified first aider at site. NO HSE - NO WORK. | 5 | 1 | 5
8 | WORKING WITH BUILDING/CEILING CRANE | 4 | 3 | 12 | 1-Maintain distance from load1- Only employees with an authorized overhead crane operator certificate can use the overhead crane; only appropriately trained and 2-Keep transport routes freequalified personnel to be used. 3-Use edge protection to prevent damage to lifting gear due tosharp edges2- Periodic inspection reports should be provided before the overhead crane is used; before the lifting operations, the visual control of 4-Prepare lifting plan if complex crane operations are to beperformedthe lifting equipment should be done and periodic control reports should be provided. 5-Lifting gear / load rigging shall be visually inspected before use3- Prepare a lifting plan if complex crane operations are to be performed; plan all crane activities in advance and prepare the set-down 6-Notify supervisor of defective lifting gear/load riggingarea. 4- Lifting gear / load rigging shall be visually inspected before use; notify supervisor of defective lifting gear / load rigging; mark the 7-Mark the defective lifting gear red and block for further use defective lifting gear red and block for further use. 8-Always monitor load and crane 5- Do a walkdown of the lift path before crane work and warn personnel working in the hazardous area. 9-Use chain hoist for small lifting operations or use chain hoist oncrane hook; use the actual crane for larger operations 6- Ensure clear and precise signals between rigger and crane operator; only the rigger shall give signals to the crane operator. 10-Do not give any direction commands while the weight isswinging from the crane hook; wait until the weight has cometo a standstill 7- Do not give any direction commands while the weight is swinging from the crane hook; wait until the weight has come to a standstill. 11-When lifting with the crane hook, take care to ensure that thechain does not become snagged 8- When lifting with the crane hook, take care to ensure that the chain does not become snagged. 12-Plan all crane activities in advance and prepare the set downarea 9- NEVER work under a suspended load; never turn your back on the load. 13-Never work under a suspended load. 10- All personnel shall clear the hazardous area if the load is to be moved above work areas; keep personnel who are not required out 14-Ensure clear and precise signals between rigger and craneoperator of the hazardous area. 15-Only the rigger shall give signals to the crane operator 11- Use chain hoist for small lifting operations or use chain hoist on crane hook; use the actual crane for larger operations. 16-Do a walk down of the lift path before crane work and warnpersonnel working in the hazardous area 12- Use edge protection to prevent damage to lifting gear due to sharp edges; maintain distance from load; keep transport routes free. 17-All personnel shall clear the hazardous area if the load is to be moved above work areas 13- Always use the correct device for lifting operations; consult your supervisor if you are uncertain. 18-Always use the correct device for lifting operations; consultyour supervisor if you are uncertain 14- PPE to be worn: Helmet EN 397, work shoes EN 345 S3, gloves EN 388, safety glasses EN 166, high-visibility vest. 19-Never turn your back on the load 15- Conduct TBT before start of work; emergency procedure to follow. NO HSE - NO WORK. 20-Use only appropriately trained and qualified personnel 21-Periodic inspection reports should be provided before the overhead crane is used. 22-Before the lifting operations, the visual control of the lifting equipment should be done and periodic control reports should be provided. 23- Only employees with authorized overhead crane operator certificate can use the overhead crane. | 4 | 1 | 4
9 | HAZARD DUE TO ELECTRICAL CURRENT, HIGH VOLTAGE | 4 | 4 | 16 | 1- Strict compliance to PTW - the electrical work permit must be taken before any electrical work; safety instructions must be a-The following precautions will be taken by the customer during Electrical Work followed. 2- Compliance with the 5 safety rules (to be applied by the customer during electrical work): Compliance with 5 safety rules: 1- Isolate 1. Isolate 2- Lock Out / Tag Out 2. Lock Out Tag Out 3- Confirm that equipment cannot be re-energized 3. Confirm that equipment cannot be re-energized 4- Grounding and short circuit 4. Grounding and short circuit 5- Maintain isolation with adjacent energized elements 5. Maintain isolation with adjacent energized elements 3- Work only under a valid permit to work prepared and issued by a person tested and authorized by the customer. b-Work permit should be taken. 4- Use only the tools appropriate for the activity; use shielded extra low voltage (PELV) or safety extra low voltage (SELV) electrical c-Safety instructions must be followed. equipment in confined areas. d-Use only the tools appropriate for the activity. 5- Only electrically trained and certified employees should work in electrical work; assign the task to a competent person. e-Use shielded extra low voltage or safety extra low voltage in confined areas 6- Wear appropriate PPE: Helmet EN 397, arc-rated protective clothing, insulated gloves, face shield / safety glasses EN 166; | 4 | 1 | 4

## 06 Step 2 cont (PDF p6)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
10 | Working with Forklift and Mobile Cranes | 4 | 3 | 12 | 1-Before using forklifts and mobile cranes, periodic control documents, periodic maintenance records, and operator certificates 1- Before using forklifts and mobile cranes, obtain periodic control documents, periodic maintenance records, and the of the employees who will use them should be obtained. operator certificates of the employees who will use them. 2-Except for the relevant operators, forklifts and mobile cranes should not be operated by other employees. 2- Third party certified operator shall operate the forklift / boom truck; the driver must have a valid driving license as per law. 3-For forklifts, reverse gear warning alarm and strobe warning light will be in working condition. 3- Except for the relevant operators, forklifts and mobile cranes should not be operated by other employees. 4-No work should be done in the mobile crane and forklift operation and maneuvering area, and personnel should be removed. 4- Daily inspection checklist to be completed by the operator before use; any defect to be reported immediately. 5-Lifting plans should be considered in lifting operations. 5- For forklifts, reverse gear warning alarm and strobe warning light in working condition; audible reverse alarm mandatory. 6- Forklift transports should be carried out considering the center of gravity of the load. 6- No work in the mobile crane and forklift maneuvering area; personnel removed; a flagman with reflective vest assigned. 7-Lifting and conveying personnel should not be done with mobile cranes, overhead cranes and forklifts without equipment 7- Lifting plans to be considered; forklift transports considering the center of gravity of the load. complying with the standards. 8- Lifting and conveying personnel shall not be done with mobile cranes, overhead cranes and forklifts without compliant 8-In order to prevent the parts from falling during lifting with forklifts, overhead cranes and mobile cranes, the parts should be equipment. lifted with durable and closed systems such as boxes and crates.9- Emergency procedure to follow; strict compliance to PTW. NO HSE - NO WORK. | 2 | 3 | 6
11 | HOT WORK(e.g., grinding, welding, cutting) | 4 | 3 | 12 | 1-Work permit must be taken before work1- Work permit must be taken before work; strict compliance to PTW and JHA requirements. 2-Mark areas and set up barricades if necessary2- Mark areas and set up barricades if necessary; remove flammable materials or provide fire-resistant shielding. 3-Remove flammable materials from the environment3- Have an observer / fire watchman available; conduct post-welding fire watch (30 min). 4-Have an observer in case of fire.4- Fire fighting equipment to be available at all times and operated by a trained person. 5-Keep fire fighting equipment with you5- Wear appropriate PPE; use full-coverage goggles or face visor for cutting, grinding, etc. 6-Wear appropriate personal protective equipment6- Oxygen and LPG / acetylene hoses to have flashback arrestors; cylinders fixed in trolleys, valve cups on when not in use. 7-Use full-coverage goggles or face visor for cutting, grinding, etc.7- Gas cylinders to be stored at least 3 meters apart from all other types; fire blankets to prevent sparks. 8- Tools inspected daily; trained workers only; TBT on correct use. NO HSE - NO WORK. | 4 | 1 | 4
12 | Field Activities Trips/Falls/Injuries | 4 | 3 | 12 | 1- Materials being transported must be stacked in an organized manner. Materials should be stacked in separate areas 1- Materials being transported must be stacked in an organized manner; materials should be stacked in separate areas according to their size and weight, ensuring they do not tip over or collapse.according to their size and weight, ensuring they do not tip over or collapse. 2- Materials should be transported using appropriate vehicles; first aid kits and fire extinguishers must be available in the 2- Materials should be transported using appropriate vehicles.vehicles. 3- Slings used for material transport must undergo visual inspection. Worn slings should not be used.3- Slings used for material transport must undergo visual inspection; worn slings should not be used. 4- Do not stand under the load while lowering materials with a crane. Do not lift loads exceeding the crane's capacity.4- Do not stand under the load while lowering materials with a crane; do not lift loads exceeding the crane's capacity. 5- Material transport and service vehicles should not be operated by anyone other than authorized personnel.5- Material transport and service vehicles should not be operated by anyone other than authorized and trained personnel. 6- First aid kits and fire extinguishers must be available in the vehicles.6- Work should not be carried out in rainy, foggy, or heavy weather; weather reports should be checked before work begins. 7- Work should not be carried out in rainy, foggy, or heavy weather; weather reports should be checked before work begins."7- Barricade and signage at material handling areas; keep transport routes free. 8- Minimum PPE: Helmet EN 397, work shoes EN 345 S3, safety glasses EN 166, gloves EN 388, high-visibility vest. 9- Conduct TBT before start of work; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
13 | PPE & Equipment | 4 | 3 | 12 | "At the start of work, all personnel's PPE assignment forms are checked using the personnel on-the-job control form. PPE 1- At the start of work, all personnel's PPE assignment forms are checked using the personnel on-the-job control form; PPE deliveries should be made in the form of notification and receipt. PPE should be checked at least once a month and the deliveries should be made in the form of notification and receipt. checks should be recorded. If employees detect any malfunction or damage to their personal protective equipment, they 2- PPE should be checked at least once a month and the checks should be recorded; if employees detect any malfunction or should inform their supervisor and ensure it is replaced.damage to their personal protective equipment, they should inform their supervisor and ensure it is replaced. 3- Minimum PPE: Minimum PPE;1- Helmet EN 397 (chin strap for teams working at height) 2- Work shoes EN 345 S3 or S1P (with sole and toe protection), safety glasses EN 166 (anti-fog), gloves EN 388 (for 1- Helmet EN 397 (chin strap for teams working at height)employees); EN 361 safety harness should be used for work at height. 3- In addition, appropriate personal protective equipment (safety harnesses, welding masks / gloves, dust masks, etc.) 2- Work shoes EN 345 ​S3 or S1P (with sole and toe protection), Safety glasses EN 166 (anti-fog), Gloves EN 388 (for according to the nature of the work should be delivered and recorded on the PPE assignment form. employees), EN361 safety harness should be used for work at height.4- Company logo work outfit should be worn. 5- Supervisor / Foreman has to make sure all crew members have the required PPE as per activity before the start of work. 3- In addition, appropriate personal protective equipment (safety harnesses, welding masks/gloves, dust masks, etc.) 6- NO HSE - NO WORK. Emergency procedure to follow. according to the nature of the work should be delivered and recorded on the PPE assignment form. 4- Company logo work The outfit should be worn." | 4 | 1 | 4

## 07 Step 2 cont (PDF p7)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
14 | Installation of Switchyard Equipment | 4 | 3 | 12 | "Before work begins, safety jump distances must be evaluated. The power should be cut off at points within the safety 1- Before work begins, safety approach / jump distances must be evaluated; the power should be cut off at points within the distance, and the 5 safety rules should be applied.safety distance, and the 5 safety rules should be applied. 1- Devices should be lifted using a mobile crane that has undergone periodic checks and has the appropriate and inspected 2- Devices should be lifted using a mobile crane that has undergone periodic checks and has the appropriate and inspected legal documents.legal documents; a crane work permit must be filled out. 2- There must be a slinger connecting the devices and a signalman directing the operation.3- There must be a slinger connecting the devices and a signalman directing the operation; only trained and qualified 3- The crane legs must be fully extended to the solid ground. In case the legs sink, materials that will expand the surface area personnel to be used. should be placed under the legs.4- The crane legs must be fully extended to the solid ground; in case the legs sink, materials that will expand the surface 4- Material guiding ropes should be used.area (pads) should be placed under the legs. 5- A crane work permit must be filled out.5- Material guiding ropes (tag lines) should be used; the operation should be carried out taking weather conditions into 6- No personnel should enter under the material under any circumstances. The work area should be restricted and warning consideration (operations suspended for winds exceeding 50 km/h). signs should be placed.6- No personnel should enter under the material under any circumstances; the work area should be restricted, barricaded 7- The operation should be carried out taking weather conditions into consideration.and fenced off with warning signs; no one other than the signalman / slinger should be in the area; the slinger / signaler 8- For all work to be done with the crane, the ""CRANE WORK CHECKLIST"" must be filled out and approved.should under no circumstances go under the lifted load. 9- During the lifting operation, the area should be restricted, and the area should be fenced off to prevent entry and exit. No 7- For all work to be done with the crane, the "CRANE WORK CHECKLIST" must be filled out and approved. one other than the signalman/slinger should be in the area. The slinger/signaler should under no circumstances go under the 8- During assembly, it should be checked whether simultaneous (top-bottom) work is being carried out; any simultaneous lifted load." work should be stopped immediately. 10- During assembly, it should be checked whether simultaneous (top-bottom) work is being carried out. Any simultaneous 9- Slingers guiding during assembly should not be under the pylon / beam / load. work should be stopped immediately. 10- Climbing the pylon should be done using a vertical lifeline and/or yo-yo; walking on the equipment should be done using 11- Slingers guiding during assembly should not be under the pylon/beam/load. a horizontal lifeline; full body harness EN 361 with double lanyard to be used. 12- Climbing the pylon should be done using a vertical lifeline and/or yo-yo, and walking on the equipment should be done 11- Minimum PPE: Helmet EN 397 with chin strap, EN 361 harness, work shoes EN 345 S3, gloves EN 388. using a horizontal lifeline.12- Conduct TBT before start of work; emergency procedure to follow; certified first aider at site. NO HSE - NO WORK. | 4 | 1 | 4
15 | WORKING IN CONFINED SPACES(inadequate evacuation and rescue possibilities, poor communicationto the outside, risk of panic attacks, poor ventilation conditions,insufficient room to move) | 4 | 3 | 12 | 1-Before starting work, the necessary work permit must be obtained.1- Confined space work permit must be obtained before work; strict adherence to PTW system. 2-Perform a visual inspection of tagging and locking for correct application before entering confined spaces2- Perform a visual inspection of tagging and locking for correct application before entering confined spaces. 3- Ambient air measurement (oxygen concentration, gas testing) should be performed before entering the enclosed space and at 3-Use only safe extra low voltage (SELV) or shielded extra low voltage (PELV) electrical equipment. regular intervals; authorized gas testing only. 4-Assign a watchman on the entrance manhole and maintain constant contact with the watchman. 4- Assign a watchman / CS attendant at the entrance manhole and maintain constant contact with the watchman; rescue 5-Check the atmosphere (oxygen concentration) before starting work, keep rescue equipment ready if necessary equipment to be kept ready if necessary. 6-Maintain order and cleanliness in confined spaces during maintenance work 5- Use only safe extra low voltage (SELV) or shielded extra low voltage (PELV) / intrinsically safe (Ex) electrical equipment inside 7-It is forbidden to work alone; Must have at least 2 employees the confined space. 8-Appropriate persons should be assigned to the job. 6- Maintain order and cleanliness (proper housekeeping) in confined spaces during maintenance work. 9-Respirator should be used if necessary 7- It is forbidden to work alone; must have at least 2 employees; appropriate persons should be assigned to the job. 10-Ambient air measurement should be performed before entering the enclosed space. 8- Respirator should be used if necessary; ventilation equipment must be available. 11-When accessing the pier, only the access point provided for this purpose should be used. 9- When accessing the pier, only the access point provided for this purpose should be used; access and exit points should be 12-Access and exit points should be clearly defined. clearly defined; emergency exits must be kept open at all times. 13-Emergency exits must be kept open at all times. 10- Hard barriers and warning signs at the entrance; first aider at site. 11- Emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
16 | Portable ladder usage | 4 | 3 | 12 | 1- Ladders must be selected according to the height at which the work will be performed.1- Ladders must be selected according to the height at which the work will be performed; ensure the ladder is long enough to safely reach the work area. 2- Ladders must have a CE Certificate with manufacturer information and a label indicating CE standards, and must 2- Ladders must have a CE Certificate and must have manufacturer information and a label indicating CE standards, comply with the EN 131 standard. and must comply with the EN131 standard. 3- Work should not exceed 30 minutes on ladders, and heavy work requiring prolonged use of equipment with both 3- Work should not exceed 30 minutes on ladders, and heavy work requiring prolonged use of equipment with both hands (cutting with a stone cutter, etc.) should not be performed. hands (cutting with a stone cutter, etc.) should not be performed. 4- Ladders should be checked before each use; inspection cards should be available and checked at least once a week. 4- Ladders should be checked before each use. Inspection cards should be available and checked at least once a 5- On type A ladders, the securing strap or locking mechanism must be completely locked when the ladder is opened; all week. locks should be properly engaged and the two sections to overlap according to the manufacturer's instructions. 5- On type A ladders, the securing strap or locking mechanism must be completely locked when the ladder is 6- Ladders with deformed, broken, or bent legs should not be used for work; ensure the ladder is in good condition, not opened. loaded beyond the maximum intended load, placed against a stable surface at the correct angle (4:1 ratio - 75 degrees). 6- Ladders with deformed, broken, or bent legs should not be used for work. 7- Contact should be made at least at 3 points on the ladder during work; work should not be done on the top two steps 7- Contact should be made at least at 3 points on the ladder during work. of the ladder. 8- Work should not be done on the top two steps of the ladder. 8- The ladder to be used for climbing must be sufficiently strong and secured by securing it at a suitable point; in cases 9- The ladder to be used for climbing must be sufficiently strong and secured by securing it at a suitable point. where securing is not reasonable or possible, ladder securing should be done according to the manufacturer's In cases where securing is not reasonable or possible, ladder securing should be done according to the instructions. manufacturer's instructions." "These tools should be used."9- PPE: Helmet EN 397 with chin strap, work shoes EN 345 S3, gloves EN 388. 10- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4

## 08 Step 2 cont (PDF p8)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
17 | WORKING WITH HAND TOOLS/POWER TOOLS /MEASURING EQUIPMENTS | 4 | 3 | 12 | 1-Only use tools which are appropriate or intended for the activity1- Only use tools which are appropriate or intended for the activity - right tool for the right job (never use a file as a lever or a 2-Visual inspection before usescrewdriver as a chisel). 3-Safety instructions in the instruction manual shall be observed2- Visual inspection before use; check the inspection tag and color code; check to ensure that safety equipment is intact; 4-Wear appropriate personal protective equipmentdefective tools to be removed from the worksite immediately. 5-Use low-vibration equipment or schedule sufficient breaks3- Safety instructions in the instruction manual shall be observed. 6-Secure tools in such a way that slipping away during operationis prevented4- Wear appropriate PPE: safety glasses EN 166 / face shield, gloves EN 388, ear plugs / muffs for noisy operations, work 7-Shield adjacent work areas if injuries to others are possibledue to flying particles or slung partsshoes EN 345 S3, Helmet EN 397. check inspection tag5- Use low-vibration equipment or schedule sufficient breaks. 8-Safety instructions in the instruction manual shall be observed6- Secure tools in such a way that slipping away during operation is prevented; shield adjacent work areas if injuries to 9-Only use tools which are appropriate or intended for the activityothers are possible due to flying particles or slung parts. 10-Check to ensure that safety equipment is intact7- Use only appropriately trained and qualified personnel. 11-Use only appropriately trained and qualified personnel8- Lines (electrical, pneumatic, compressed and process air) shall be safely routed and secured. 12-Lines (electrical, pneumatic, compressed and process air) shallbe safely routed and secured9- If hydraulic fluid is used, follow the instructions in the safety data sheet or the operating instructions; use whip check when 13-If hydraulic fluid is used, follow the instructions in the safety data sheet or the operating instructionsusing hydraulic and pneumatic systems. 14-Wear appropriate personal protective equipment 10- Conduct TBT before start of work; emergency procedure to follow. NO HSE - NO WORK. 15-Use whipcheck when using hydraulic and pneumatic systems. | 4 | 1 | 4
18 | HAZARD DUE TO FALLING | 4 | 3 | 12 | 1-Installation of scaffolding or barriers, only access scaffoldingthat has been inspected and approved1- Installation of scaffolding or barriers; only access inspected and approved scaffolding (green label). 2-Observe work instruction on use of PPE to prevent falling!2- Use PPE to prevent falling (full body harness EN 361 with 100% tie-off where required). 3-Use PPE to prevent falling3- Use tool lanyards / keepers, toe boards and mesh under platforms; barricade the area below. 4- Minimum PPE: Helmet EN 397 with chin strap, work shoes EN 345 S3, gloves EN 388. NO HSE - NO WORK. | 4 | 1 | 4
19 | HAZARD DUE TO SLIPPING, STUMBLING AND FALLING ON SAME LEVEL | 3 | 3 | 9 | 1- Lay cables outside the hazard zone; cables and hoses neatly routed and secured to prevent slips and trips. 1-Lay cables outside the hazard zone 2- Materials and tools not required shall be removed; maintain housekeeping standards at all times. 2-Materials and tools which are not required shall be removed from the work area 3- Traffic routes shall be kept clear; walkways free of obstruction; remove water / oil spills immediately. 3-Traffic routes shall be kept clear 4- Make sure there is no deformation, lubrication or gap on the floor; non-slip mats and drainage where required. 4-Keep the work area clean and tidy 5- Adequate lighting; proper footwear (work shoes EN 345 S3 with anti-slip sole) to be worn. 5-Make sure that there is no deformation, lubrication or gap on the work area floor, and take the necessary precautions, if 6- Signage where temporary hazards exist; emergency procedure to follow. NO HSE - NO WORK. any. | 3 | 1 | 3

## 09 Step 2 cont (PDF p9)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
20 | HAZARD DUE TO WORK WITH BUILDING/CEILINGCRANE/LIFTING GEAR/LIFTING ACCESSORIES AND WORK WITH SUSPENDED LOADS | 4 | 3 | 12 | 1- Lifting gear / load rigging shall be visually inspected before use; check inspection tags for validity; mark 1-Barricade off work area if necessarydefective lifting gear and block for further use; notify supervisor of defective lifting gear / slings. 2-Use chain hoist for rolling parts in and out2- Slings and shackles capable of supporting 1.25 times the weight of the load to be lifted must be used, and the 3-Use crane for larger operations, also use chain hoist ifnecessaryslings and shackles must have label certificates (valid third-party certification, color coded). Worn or damaged 4-Use provided devicesequipment without labels should not be used. 5-Use edge protection to prevent damage to lifting gear due tosharp edges3- Slings must be attached at the appropriate angle; protective pads must be used at points where they come into 6-Use all load attachment rigging correctlycontact with sharp surfaces; equipment must be checked for deformation before each operation. 7-Do not work under suspended loads4- Use all load attachment rigging correctly; use provided devices; use edge protection to prevent damage to lifting 8-Lifting gear / load rigging shall be visually inspected before usegear due to sharp edges. 9-Check inspection tags for validity5- Do not work under suspended loads; maintain distance from load; keep transport routes free. 10-Mark defective lifting gear and block for further use6- Do a walkdown of the lift path before crane work and warn personnel working in the hazardous area; plan all 11-Notify supervisor of defective lifting gear/ slingscrane activities in advance and prepare the set-down area. 12-Maintain distance from load7- Ensure clear and precise signals between rigger and crane operator; never turn your back on the load. 13-Keep transport routes free8- All personnel shall clear the hazardous area if the load is to be lifted above work areas; keep personnel who are 14-Do a walkdown of the lift path before crane work and warn personnel working in the hazardous areanot required out of the hazardous area. 15-Plan all crane activities in advance and prepare the setdownarea9- Always use the correct device for lifting operations; consult your supervisor if you are uncertain; use only 16-Never turn your back on the loadappropriately trained and qualified personnel. 17-Ensure clear and precise signals between rigger and crane operator10- Wear appropriate personal protective equipment (high-visibility safety vest if necessary); Helmet EN 397, work 18-All personnel shall clear the hazardous area if the load is to belifted above work areasshoes EN 345 S3, gloves EN 388. 19-Always use the correct device for lifting operations; consultyour supervisor if you are uncertain11- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. 20-Keep personnel who are not required out of the hazardousareaUse only appropriately trained and qualified personnel 21-Wear appropriate personal protective equipment (yellow safetyvest if necessary) | 4 | 1 | 4
21 | HAZARD DUE TO ENTERING, EXITING Confined Space | 4 | 3 | 12 | 1- When accessing confined space, use only the access point provided for this purpose; clearly define access and exit points. 1-When accessing scaffolding, use only the access pointprovided for this purpose2- Keep emergency exits clear at all times; adequate lighting at entry / exit points. 2-Clearly define access and exit points3- A CS attendant / watchman to be available at entry and exit area; barricade the work area. 3-Keep emergency exits clear at all times4- Keep the work area free from oil; proper housekeeping. 4-Keep work area free from oil5- Minimum PPE as per activity; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
22 | HAZARD DUE TO UNRESTRICTED AREA | 3 | 3 | 9 | 1- Barricade off the work area (hard barricading); keep personnel who are not required out of the hazardous area. 1-Barricade off work area if possible.2- Use warning signs and safety tape; mark the area before the start of work. 2-Keep personnel who are not required out of the hazardous area3- Use only appropriately trained and qualified personnel; security to control access points with valid ID cards. 3-Use only appropriately trained and qualified personnel4- Inform subcontractors of the risks in shared areas; conduct TBT. NO HSE - NO WORK. | 3 | 1 | 3
23 | Working with Manlifts | 4 | 3 | 12 | 1- Manlifts should only be used by experienced and authorized/trained operators. A trained personnel familiar with the ground 1- Manlifts should only be used by experienced and authorized / trained operators; a trained person familiar with the ground rescue plan must be present while working at height on the manlift.rescue plan must be present while working at height on the manlift. 2- Visual checks must be performed by the user before each operation.2- Visual checks must be performed by the user before each operation; periodic inspection reports to be available. 3- Proper use of PPE (Personal Protective Equipment) in accordance with working at height regulations must be ensured.3- Before starting work, the ground must be checked to ensure it is stable and level; work should absolutely not be done on 4- Before starting work, the ground must be checked to ensure it is stable and level. Work should absolutely not be done on slippery surfaces. slippery surfaces. When changing positions, there should be no obstacles, gaps, cables, or hoses along the route that could 4- When changing positions, there should be no obstacles, gaps, cables, or hoses along the route that could cause tipping; cause tipping; the scissors must be in the closed position.the scissors must be in the closed position. 5- Wheel locks and support legs must be used to prevent the manlift from moving during operation.5- Wheel locks and support legs must be used to prevent the manlift from moving during operation. 6- The capacity of the basket (Safe Working Load) must not be exceeded; it should only be used to lift workers and hand 6- The capacity of the basket (Safe Working Load) must not be exceeded; it should only be used to lift workers and hand tools. Maximum load information must be clearly visible on the equipment.tools; maximum load information must be clearly visible on the equipment. 7- Limit switches must not be modified or deactivated.7- Limit switches must not be modified or deactivated; do not climb on or stand on the guardrails of the manlift. 8- Do not climb on or stand on the guardrails of the manlift.8- At the end of the shift, the machines must be locked and placed on a solid and level surface where there are no obstacles 9- At the end of the shift, the machines must be..." The machines must be locked. The machines must be placed on a solid or movement; the platform must be lowered, the ignition key removed and kept in a place inaccessible to unauthorized and level surface where there are no obstacles or movement. The platform must be lowered, the ignition key removed and persons, and chocks must be placed under the wheels. kept in a place inaccessible to unauthorized persons, and chocks must be placed under the wheels.9- If welding is to be performed during operation, the welding frame must not come into contact with the machine; external 10- If welding is to be performed during operation, the welding frame must not come into contact with the machine. External grounding of the body must be provided. grounding of the body must be provided. 11- When working on the manlift, attention must be paid to exposed power cables 10- When working on the manlift, attention must be paid to exposed power cables and electrical trays, and a safe working and electrical trays, and a safe working distance must be maintained.distance must be maintained. 11- PPE: Helmet EN 397 with chin strap, full body harness EN 361 with double lanyard, work shoes EN 345 S3. 12- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4

## 10 Step 2 cont (PDF p10)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
25 | HAZARD DUE TO FIRE OR EXPLOSION | 4 | 3 | 12 | 1- Only use tools which are suitable or intended for the activity; visual inspection before use. 1-Only use tools which are suitable or intended for the activity2- Remove hoses from combustible gases and oxygen or disconnect from the supply point when work is interrupted. 2-Remove hoses from combustible gases and oxygen ordisconnect from supply point when work is interrupted3- Maintain a distance of at least 3 meters between fuel gases and oxidation gases or provide for a fire-resistant partition. 3-Maintain a distance of at least 3 meters between fuel gasesand oxidation gases or provide for a fire-resistant partition4- ATTENTION: Liquid gas cylinders (propane or butane) shall be stored at least 3 meters from ALL other types of gas 4-Safety instructions in the instruction manual shall be observedcylinders. 5-Visual inspection before use5- NO SMOKING in the oil storage area. 6-Remove fire loads, assign fire watches, provide forextinguishing agents6- Remove fire loads, assign fire watches, and provide for extinguishing agents; fire extinguishers to be available at all times 7-ATTENTION! Liquid gas cylinders (propane or butane) shall bestored at least 3 meters from ALL other types of gas and operated by a trained person. cylinders7- Safety instructions in the instruction manual shall be observed; wear appropriate PPE. 8-NO SMOKING in oil storage area8- Good housekeeping to avoid accumulation of combustible waste. 9-Wear appropriate personal protective equipment9- Conduct TBT; emergency procedure to follow; certified first aider at site. NO HSE - NO WORK. | 4 | 1 | 4
26 | HAZARD DUE TO FALLING LOADS | 4 | 4 | 16 | 1- Barricade off the work area; keep personnel who are not required out of the hazardous area. 1-Barricade off work area 2- Suspend the load in accordance with drawing specifications; competent rigger / slinger to attach the load. 2-Suspend load in accordance with drawing specifications 3- NEVER work under a suspended load; no personnel under the load under any circumstances. 3-Keep personnel who are not required out of the hazardous area 4- Lifting gear visually inspected before use; defective gear withdrawn from service. NO HSE - NO WORK. 4-When working at height, all hand tools should be kept in the keeper. | 4 | 1 | 4
27 | Waste Management | 3 | 3 | 9 | 1- Waste sorted per waste group and class (metal, cable, wood, paper) in designated waste area. 2- Containers with proper lids; timely evacuation of waste; proper housekeeping. 1-Waste must be sorted according to waste group (metal, cable, wood, paper, etc.). 3- Hazardous waste segregation; MOTAT records maintained; licensed disposal per MSDS. 2-Waste must be sorted according to waste class and disposed of in the waste area. 4- Emergency procedure to follow. NO HSE - NO WORK. | 3 | 1 | 3

## 11 Step 2 cont (PDF p11)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
28 | HAZARD DUE TO POOR ILLUMINATION | 3 | 3 | 9 | 1- Illumination must be increased according to conditions; adequate lighting to be ensured in all work areas before the start of work. 1- Illumination must be increased according to conditions 2- Defective lighting to be repaired / replaced immediately; personal head lamps for night / low-light tasks. 2-Lighting that is appropriate to the situation shall be provided 3- Signage to mark hazards in low-light areas; housekeeping maintained. NO HSE - NO WORK. | 3 | 1 | 3
29 | Lifting Operation | 4 | 3 | 12 | 1- The weight of the material to be lifted must be known before lifting, and the crane must be selected according to the weight 1- The weight of the material to be lifted must be known before lifting, and the crane must be selected according to the weight of the of the material to be lifted.material; loads must not exceed the S.W.L. of the crane or the slings. 2- The lifting accessories to be used must have appropriate capacities and must be in a safe condition without deformation, with valid 2- The lifting accessories to be used must have appropriate capacities and must be in a safe condition without deformation. third-party certification and color code. 3- Unauthorized personnel should not be present in the work area. 3- Unauthorized personnel should not be present in the work area; the lifting area must be marked, barricaded and a warning sign 4- The crane must undergo periodic inspection, the operator must have a certificate and it must be checked. must be placed. 5- The lifting area must be marked and a warning sign must be placed. 4- The crane must undergo periodic inspection, the operator must have a valid certificate, training and experience (TPI certified) and 6- The crane's equipment must be checked and not overloaded beyond its tonnage. it must be checked; the daily crane inspection sheet to be completed. 7- The crane's legs must be extended, the ground checked and ensured to be level, and the crane's outriggers and pads must 5- The crane's legs must be extended, the ground checked and ensured to be level, and the crane's outriggers and pads must be be used to adapt to the ground. used to adapt to the ground; ensure the crane setting by trial lift; soil condition to be assessed with strength calculation if required. 8- Weather risks must be assessed (Reminder: In case of winds exceeding 50 km/h, all operations are suspended). 6- Weather risks must be assessed - in case of winds exceeding 50 km/h (lifting plan wind limit 9.5 m/s), all operations are 9- The necessary distance between the load and the operators must be provided and the personnel must be informed. suspended. 10- The operation of the signal warning lights must be checked.7- The necessary distance between the load and the operators must be provided and the personnel must be informed; the operation 11- Absolutely no one should go underneath the material. If necessary, a rope/cord should be used for guidance. of the signal warning lights must be checked. 12. When securing the material, if the material has sharp edges, cardboard or similar material should be placed under the 8- Absolutely no one should go underneath the material; if necessary, a rope / cord (tag line) should be used for guidance. material to prevent damage to the slings; care should be taken. 9- When securing the material, if the material has sharp edges, cardboard or similar material should be placed under the material to 13. No load exceeding the tonnage of the slings should be attached.prevent damage to the slings; no load exceeding the tonnage of the slings should be attached. 10- The lifting operation must be controlled by the signalman (banksman); if visual contact is not possible, communication between 14. The lifting operation must be controlled by the signalman. If visual contact is not possible, communication between the the crane operator and the signalman should be ensured by providing them with a radio. crane operator and the signalman should be ensured by providing them with a radio. 11- All personnel performing the operation must wear all necessary appropriate PPE (Helmet EN 397 with chin strap, high-visibility 15. All personnel performing the operation must wear all necessary appropriate personal protective equipment. vest, work shoes EN 345 S3, gloves EN 388). 16. When bringing the panels into the control building, they must be lowered due to the door height; this operation must be 12- When bringing the panels into the control building, they must be lowered due to the door height; this operation must be done with done with the help of a crane. the help of a crane; the slings used to lift the panels must be suitable for the weight of the panels, and deformed slings must 17. The slings used to lift the panels must be suitable for the weight of the panels, and deformed slings must absolutely not absolutely not be used. be used. 13- Ensure the approved lifting plan, PTW and other relevant documents are available for the lifting activity; continuous supervision by the lifting supervisor. 14- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
30 | Cable pulling | 4 | 3 | 12 | 1- When removing the cable reel from the truck, a sling appropriate for the weight of the material must be used. 2- A qualified crane operator must be used; the crane's lifting apparatus must be checked; the slinger-signaler must direct the operation; When removing the cable reel from the truck, a sling appropriate for the weight of the material must be used.outriggers sufficiently spread with pads under them. 3- No one should be in the area of operation or under the material; a guide rope must be used, warnings given, and a lookout present. A crane operator must be used, the crane's lifting apparatus must be checked, the slinger-signaler must direct the operation, 4- The cable reel must be set up on a level surface using a cable stand suitable for its tonnage; enough personnel at the head of the the crane's outriggers must be sufficiently spread apart, and pads must be placed under the outriggers to ensure stability on reel to turn it. the ground. No one should be in the area of operation, no one should enter under the material, a guide rope must be used, the 5- No one should stand in front of the cable reel when the fiber guide is pulled through the laid pipes, as the end is hard. necessary warnings must be given, and a lookout must be present. 6- The cable pulling device must be anchored to the ground with dowels; the area enclosed with railings and barriers. The cable reel must be set up on a level surface using a cable stand suitable for the tonnage of the cable reel. 7- Cable reels should be fixed inside the manholes; manholes cordoned off with tape and covered at the end of the shift. There must be a sufficient number of personnel at the head of the cable reel to turn the reel. 8- Number of personnel for cable pulling to be appropriate; communication via telephone / radio; cable cutters used for cutting. No one should stand in front of the cable reel when the fiber guide is being pulled through the laid pipes, as the end is hard.9- All ladders, platforms, or scaffolding used must be inspected by a competent person, certified with a green card, and comply with The cable pulling device must be anchored to the ground with dowels. The area must be enclosed with railings and barriers.standards. All ladders, platforms, or scaffolding used for cable pulling must be inspected by a competent person, certified with a green 10- Cable pulling device and reel transport stands to have periodic inspection reports from competent institutions within the last year. card, and comply with standards.11- Where energized MV cables are located, protection to be worn and insulating mats laid in the channel. 12- Minimum PPE (Helmet EN 397, work gloves EN 388, safety glasses EN 166, reflective vest, work shoes EN 345 S3); boots due to The cable pulling device and reel transport stands must have periodic inspection reports issued by competent institutions rainwater / sewage in manholes. within the last year. 13- Conduct TBT; emergency procedure to follow; certified first aider at site. NO HSE - NO WORK. | 4 | 1 | 4
31 | HAZARD DUE TO UNINTENTIONALACTIVATION/INCORRECT OPERATION OFSYSTEMS/COMPONENTS | 4 | 3 | 12 | 1- Permit to work prepared and issued only by a person tested and authorized by the customer. 1-Permit to work has been issued 2- Ensure communication with all participating persons before activation and operation. 2-NOTE: Permit to work shall be prepared and issued only byperson tested and authorized by the customer 3- Deactivate pumps before checking oil strainers; LOTO to be applied for all energy isolation. 3-Ensure communication with all participating persons beforeactivation and operation 4- Electrical isolation by authorized and competent personnel; tested and verified with approved devices. 4-Deactivate pumps before checking oil strainers. 5- Only authorized and competent personnel to operate systems / components. NO HSE - NO WORK. | 4 | 1 | 4
32 | HAZARD DUE TO HANDLING OF INSULATING MATERIAL | 4 | 3 | 12 | 1- Keep personnel who are not required out of the work area; barricade the work area. 1-Keep personnel who are not required out of the work area 2- Wear protective clothing and respirator masks (FFP3) per the material MSDS. 2-Wear protective clothing and respirator masks. 3- Minimize dust generation; local exhaust ventilation where necessary. NO HSE - NO WORK. 3-Use fall protection equipment when necessary. | 4 | 1 | 4
| HAZARD DUE TO UNAUTHORIZED PERSONS/ |  |  |  | 1- Mark areas and barricade off or set up warning signs; hard barricading in high-risk zones. 1-Mark areas and barricade off if necessary or set up warningsigns.

## 12 Step 2 cont (PDF p12)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
34 | Assembly of Primary Equipment - Crane operations, use of slings and shackles. | 4 | 3 | 12 | 1- Lifting accessories must be stored in a way that prevents damage or deterioration.1- Lifting accessories must be stored in a way that prevents damage or deterioration; ropes, slings, and chains must be replaced 2- Ropes, slings, and chains must be replaced when deformation occurs. Their certifications must be recorded.when deformation occurs and their certifications must be recorded. 3- Slings and shackles capable of supporting 1.25 times the weight of the load to be lifted must be used, and the slings and 2- Slings and shackles capable of supporting 1.25 times the weight of the load to be lifted must be used, and the slings and shackles must have label certificates. Worn or damaged equipment without labels should not be used. shackles must have label certificates. Worn or damaged equipment without labels should not be used. 3- Slings must be attached at the appropriate angle; protective pads must be used at points where they come into contact with 4- Slings must be attached at the appropriate angle. sharp surfaces; equipment must be checked for deformation before each operation. 5- Protective pads must be used at points where they come into contact with sharp surfaces. 4- Personnel must use double lanyards (full body harness EN 361) when climbing pylons to install beams and remove slings; it 6- Equipment must be checked for deformation before each operation. must be absolutely ensured beforehand that the areas where the lanyards will be attached are securely created. 7- Personnel must use double lanyards when climbing pylons to install beams and remove slings. It must be absolutely 5- Long slings should be used to ensure that the slings stay close to the pylon during beam installation, preventing personnel ensured beforehand that the areas where the lanyards will be attached are securely created. from walking on the beam. If short slings are used, personnel will attach to the yo-yo, which is fixed to the crane hook, to remove 8- Long slings should be used to ensure that the slings are close to the pylon during beam installation, preventing personnel the slings. from walking on the beam. If short slings are used, personnel will attach to the yo-yo, which is fixed to the crane hook, to 6- Ascending the pylon should be done using a vertical lifeline and/or yo-yo; walking on the equipment should be done using a remove the slings. horizontal lifeline. 9- Ascending the pylon should be done using a vertical lifeline and/or yo-yo / Walking on the equipment should be done using 7- Only trained and competent rigger / banksman; radio communication for blind areas; continuous supervision. a horizontal lifeline. 8- Minimum PPE: Helmet EN 397 with chin strap, EN 361 harness with double lanyard, work shoes EN 345 S3, gloves EN 388. 9- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
35 | Current Transformer, Voltage Transformer, Surge Arrester Installation of Supports | 4 | 3 |  | 1- Before starting ground assembly work, the work area must be prepared and organized; factors that could cause slipping, 1- Before starting ground assembly work, the work area must be prepared and organized; slip, trip and fall factors eliminated. tripping, and falling must be eliminated.2- Sling attachment at the supports at the top, with a protective pad under the sling to prevent damage. 2- Sling attachment at the supports should be done at the top, and a protective pad or similar piece should be used under the 3- Personnel must work with a safety harness (EN 361) where work at height is involved. sling to prevent damage.4- After assembly, the sling retrieved from the top using an appropriate ladder (per portable ladder requirements). 3- Personnel must work with a safety harness.5- Work permit to be obtained before work; strict compliance to PTW requirements. 6- Minimum PPE: Helmet EN 397, work shoes EN 345 S3, gloves EN 388, safety glasses EN 166. 4- After the support assembly is complete, the sling should be retrieved from the top using an appropriate type of ladder. 7- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
36 | WILD ANIMAL BITES / EXPOSURE TO DISEASE- CARRYING VOLATILES | 2 | 4 | 8 | In mild injuries, the wound should be washed with soap and cold water for 5 minutes. The wound should be covered with a 1- In mild injuries, the wound should be washed with soap and cold water for 5 minutes and covered with a clean cloth. In case of clean cloth. If there is serious injury and bleeding, the bleeding should be stopped by applying pressure to the wound with a serious injury and bleeding, the bleeding should be stopped by applying pressure to the wound with a clean cloth and support should be received immediately from 112. clean cloth and support should be received immediately from 112. Panzeir status for wild animals belonging to the study area 2- The venomous animal situation for wild animals belonging to the study area should be learned from health centers; the worker should be learned from health centers. The worker should be transferred to the hospital in possible snake bites and it should should be transferred to the hospital in possible snake bites and it should be ensured that snake serum is intervened against snake be ensured that snake serum is intervened against snake bites. bites. 3- Comprehensive information on common local vectors and diseases should be collected; if necessary, special expertise should • Comprehensive information on common local carriers and diseases should be collected. If necessary, special expertise be acquired at the first stage. should be acquired at the first stage. 4- Personnel to be trained in first aid; first aid kit to be available; certified first aider at site. • Personal behavioral training should be provided. (e.g. food disposal, clothing, fly repellents) 5- Emergency Iraqi numbers (112) must be available; all personnel familiar with the emergency procedure. • Mechanical vector control measures should be taken. (eg mosquito screens, mosquito nets) 6- Personal behavioral training should be provided (e.g., food disposal, clothing, fly repellents); mechanical vector control • Reproduction control should be done. (eg disposal of still water) measures should be taken (e.g., mosquito screens, mosquito nets); reproduction control should be done (e.g., disposal of still • Chemical or biological vector should be controlled. (applied by experts) water); chemical or biological vectors should be controlled (applied by experts). • If there is a deficiency in routine vaccination, it should be completed, if possible and necessary, additional immunization 7- If there is a deficiency in routine vaccination, it should be completed; if possible and necessary, additional immunization should should be done. be done. • While driving, you should be careful about the possibility of wild or domestic animals on the road.8- Inspect personal clothing and PPE before use for presence of scorpions; inspect the working area for presence of venomous animals and insects. 9- While driving, be careful about the possibility of wild or domestic animals on the road. | 1 | 4 | 8

## 13 Step 2 cont (PDF p13)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
37 | Cable laying | 4 | 3 | 12 | "When removing the cable reel from the truck, a sling suitable for the tonnage of the material must be used.1- When removing the cable reel from the truck, a sling suitable for the tonnage of the material must be used. The crane must be operated by an operator, the lifting apparatus of the crane must be checked, the sling operator/signaler must direct 2- The crane must be operated by a qualified operator; the lifting apparatus of the crane must be checked; the sling operator / signaler the operation, the crane's outriggers must have sufficient clearance and pads must be placed under the legs for adaptation to the must direct the operation; the crane's outriggers must have sufficient clearance and pads must be placed under the legs for adaptation ground. No one should be in the operation area, absolutely no one should go under the material, and a guide rope must be used, to the ground. necessary warnings must be given, and a lookout must be present.3- No one should be in the operation area; absolutely no one should go under the material; a guide rope must be used, necessary The cable reel must be set up on a flat surface using a cable stand suitable for its tonnage.warnings must be given, and a lookout must be present. There must be enough personnel at the head of the cable reel to turn the reel.4- The cable reel must be set up on a flat surface using a cable stand suitable for its tonnage; there must be enough personnel at the head of the cable reel to turn the reel. No one should stand in front of the fiber guide when it is being driven through the laid pipes because its tip is hard. 5- No one should stand in front of the fiber guide when it is being driven through the laid pipes because its tip is hard. The cable pulling device must be fixed to the ground with dowels. The area must be enclosed with railings and barriers. 6- The cable pulling device must be fixed to the ground with dowels; the area must be enclosed with railings and barriers. The cable pulling device and reel carrying stands must have a periodic inspection report issued by competent institutions within the last 7- The cable pulling device and reel carrying stands must have periodic inspection reports issued by competent institutions within the year. last year. Arc protection must be worn and insulating mats must be laid in the channel where energized MV cables are located." 8- Cable reels should be fixed inside the manholes, and the cable should be pulled through them; manholes should be cordoned off with "Cable reels should be fixed inside the manholes, and the cable should be pulled through them. tape and covered at the end of the shift. Manholes should be cordoned off with tape and covered at the end of the shift. 9- The number of personnel for cable pulling should be appropriate for the operation, and communication should be via telephone; cable The number of personnel for cable pulling should be appropriate for the operation, and communication should be via telephone. cutters should be used for cable cutting. Cable cutters should be used for cable cutting. 10- Where energized MV cables are located, protection must be worn and insulating mats must be laid in the channel. Personal protective equipment should be worn and used. (Helmet, work gloves, safety glasses, reflective vest, work shoes) Boots 11- Personal protective equipment should be worn and used (Helmet EN 397, work gloves EN 388, safety glasses EN 166, reflective should be worn due to the accumulation of rainwater and sewage water inside the manhole." vest, work shoes EN 345 S3); boots should be worn due to the accumulation of rainwater and sewage water inside the manhole. 12- Conduct TBT; emergency procedure to follow; certified first aider at site. NO HSE - NO WORK. | 4 | 1 | 4
38 | Switchyard Circuit Breaker Installation Work | 4 | 3 | 12 | Before work begins, site officials must conduct a site survey to identify hazards and risks. Work should not commence without 1- Before work begins, site officials must conduct a site survey to identify hazards and risks; work not to commence without taking necessary precautions.necessary precautions. -Before mechanical assembly work begins, appropriate work permits must be obtained and work permit requirements must be 2- Before mechanical assembly work begins, appropriate work permits must be obtained (strict compliance to PTW). 3- Work at height requirements per the "Loading the primary material to the site" work step to be ensured (EN 361 harness, met. 100% tie-off). -Work at height requirements specified in the "Loading the primary material to the site" work step must be ensured. 4- Crane use and safety precautions per the "Mechanical assembly work" work step to be ensured (certified crane, signalman, -Crane use and safety precautions specified in the "Mechanical assembly work" work step must be ensured. barricading). -Materials will be lifted using 2 slings and by lowering them from the upper section; precautions will be taken against material 5- Materials to be lifted using 2 slings and lowered from the upper section; precautions against tipping / tilting (tag lines, tipping, tilting, etc. competent rigger). 6- Power cut off within safety distance; 5 safety rules applied (Isolate, LOTO, verify, ground, isolate). The power must be cut off at points within the safety distance, and the 5 safety rules must be applied." 7- Minimum PPE: Helmet EN 397 with chin strap, EN 361 harness, work shoes EN 345 S3, gloves EN 388. 8- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
39 | Landscaping and Excavation Works | 4 | 3 | 12 | 1- The licenses, maintenance records, and other legal documents for trucks and construction equipment (JCS, Loader, 1- Licenses, maintenance records and legal documents for trucks and construction equipment to be provided. Excavator, etc.) to be used on site must be provided.2- Drivers' personal documents submitted; valid driving license and on-the-job training; certified driver / operator only. 2- Drivers' personal documents must be submitted, and they must receive on-the-job training.3- Observer / flagman with reflective vest in the maneuvering area; audible reverse alarm installed. 3- An additional observer must be present in the maneuvering and working area of trucks and construction equipment.4- Workers must be prevented from entering the truck's blind spot; training to be provided. 4- Workers must be prevented from entering the truck's blind spot, and training must be provided to workers on this subject.5- No one near the truck when loading excavated material; equipment to prevent spilling. 5- No one should be near the truck when loading excavated material onto it.6- Live wires / cables identified before excavation; excavation certificate and scanning report attached. 6- Excavated material must be transported to the area indicated by the customer.7- Side-wall protection for excavations over 1.2 m; spoil kept 1.5 m from the edge; two clear accesses. 7- Equipment must be available on trucks to prevent excavated material from spilling.8- Water accumulation to be pumped out immediately (de-watering); barricade and warning signs erected. 9- Minimum PPE: Helmet EN 397, work shoes EN 345 S3, safety glasses EN 166, gloves EN 388, high-visibility vest. 10- Conduct TBT; emergency procedure to follow; certified first aider at site. NO HSE - NO WORK. | 4 | 1 | 4
40 | General field activities - Working near energized points | 4 | 3 | 12 | 1- Energized areas must be restricted using appropriate barriers, tape, etc.1- Energized areas restricted with barriers, tape and warning signs; clear identification of live equipment. 2- Work must be performed using equipment that will not approach the safety distance (excavators, etc.). The safety distance 2- Work with equipment that will not approach the safety distance; safety distance calculated prior to work. must be calculated prior to work.3- Energy shutdown; 5 safety rules applied (Isolate, LOTO, verify, ground, maintain isolation). 3- Energy shutdown must be requested for work within the safety distance, and the 5 safety rules must be applied.4- Employees must be trained on energy points; verify line status before work; maintain safe clearance. 4- Employees must be trained on energy points.5- Employees must not raise materials upwards near energized points. 5- Employees must not raise materials they are holding upwards 6- Minimum PPE: insulated gloves where required, Helmet EN 397, face shield EN 166, work shoes EN 345 S3. 7- Conduct TBT; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4
41 | Emergency situation | 4 | 3 | 12 | 1-An emergency action plan should be organized and communicated to all employees. 1- An emergency action plan should be organized and communicated to all employees. 2-Teams that will respond to emergencies should be identified (first aid team, fire team, search and rescue team, evacuation 2- Teams that will respond to emergencies (first aid team, fire team, search and rescue team, evacuation team, etc.) should team, etc.) and trained, and the training provided should be recorded. be identified and trained, and the training provided should be recorded. 3-The list of names and contact information for emergency response teams must be posted in a visible location in the work 3- The list of names and contact information for emergency response teams must be posted in a visible location in the work area and mobilization area. area and mobilization area (112, nearest hospital, response times). 4-The contents of the first aid and emergency kits must be determined by the occupational safety specialist and technical 4- The contents of the first aid and emergency kits must be determined by the occupational safety specialist and technical authorities, procured, and kept on site.authorities, procured, and kept on site. 5- Every worker on the construction site should be given an ID card. The back of the ID card should contain the project 5- Every worker on the construction site should be given an ID card; the back of the ID card should contain the project emergency numbers, and the front should contain the employee's identity information and the training they have received.emergency numbers, and the front should contain the employee's identity information and the training they have received. 6- Certified first aider must be available at site at all times; emergency procedure to follow. NO HSE - NO WORK. | 4 | 1 | 4

## 14 Step 2 cont (PDF p14)
No | Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | Assessment / Değerlendirme High (H)
|  | Likelihood (L) | Severity (S) | Risk Score(R) |  | Likeliho od (L) | Severity (S) | Risk Score(R)
43 | Working with Chemicals | 4 | 3 | 12 | 1-Chemicals that are harmless to health should be chosen.1- Chemicals that are harmless to health should be chosen; use taking into account the MGBF. 2-It should be used taking into account the MGBF.2- Chemical wastes to be disposed of according to legal and local rules. 3-Chemical wastes should be disposed of according to legal and local rules.3- Spilled chemicals to be cleaned immediately with absorbent and cleaning materials. 4-Spilled chemicals should be cleaned immediately with absorbent and cleaning materials.4- If hydraulic fluid is used, it must be used in accordance with the MSDS form. 5-If hydraulic fluid is used, it should be used in accordance with the MSDS form.5- Chemicals to be stored at a minimum level; MSDS to be available at the work area and explained during TBT. 6-It should be stored at a minimum level.6- To avoid exposure to chemical fumes, dust or fog: suction of the air, cleaning the air or protective masks. 7-In order not to be exposed to chemical fumes, dust or fog, suction of the air in the environment, cleaning the air or protective 7- Personal Protective Equipment specified in the MSDS of chemicals to be used (FFP3 masks, gloves, protective clothing). masks should be used.8- If chemicals spill or leak, clean with absorbent kits. NO HSE - NO WORK. 8-Personal Protective Equipment specified in the MSDS of chemicals should be used. 9-If chemicals spill or leak into an environment, they should be cleaned with absorbent kits. | 2 | 3 | 6

## 15 Steps 3-4-5 Signatures
No | Pathway of activity / |  |  |  | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions | [7 empty] | Assessment / Değerlendirme High (H)
[5 empty] | Likelihood (L) | Severity (S) | Risk Score(R) | [8 empty] | Likeliho od (L) | Severity (S) | Risk Score(R)
STEP 3 / | PPE & Equipment
Equipment PPE & | LOTO | EN 397 Helmets | EN 352 Ear Plug | EN 345 S3 Safety Shoes | EN 388 Mechanical | EN 407 Heat- Tolerant Glove | Protective Clothing | EN 166 Eye wear | EN 166 Face Shield | EN 407 Thermo Safety Glove | EN 361 Full Body Harness | Electric Arc Protective Clothing | Electrical Safety Gloves | EN 136 Dust Mask |  | Reflective Vest | Fire Extinguishe r | Other
No Follow Path the | Electrical work if neccessary | All | All | All | All |  | All | All |  |  | Working at height | Electrical work if neccessary | Electrical work if neccessary |  |  | All | All
STEP 4 / | HEAD of PROJECT MANAGER |  |  |  | QUALITY MANAGER |  |  |  | PROJECT MANAGER | [5 empty] | EHS
Approval / Onay | Name Surname: UĞUR AKBULUT Date: Signature Phone |  |  |  | Name Surname: ABDURRAHMAN ÖĞÜT Date : Ogut Digitally signed by Ogut Abdurrah Abdurrahman Signature Date: 2026.03.04 man 11:53:38 +03'00' Phone |  |  |  | Name Surname: ONUR ÖZVATAN Date: Signature Phone |  |  | SUITABLE | Name Surname : DOĞUKAN ARANDI Date: Arandi Dijital olarak imzalayan Arandi Dogukan DN: cn=Arandi Dogukan, o=Siemens, Dogukan email=dogukan.arandi@siemens- Signature energy.com Tarih 2026.03.04 11:18:39 +03'00' Phone |  |  |  |  | SUITABLE
[12 empty] | UNSUTABILE | [5 empty] | UNSUTABILE
STEP 5 | TRAINER/SIGN | [8 empty] | TRAINING AREA |  |  |  | TRAINING DATE
Name Surname Signature
Personnel Signatures |  |  |  |  | 6. |  |  |  | 11. |  |  |  |  | 16.
[5 empty] | 7. |  |  |  | 12. |  |  |  |  | 17.
[5 empty] | 8. |  |  |  | 13. |  |  |  |  | 18.
| 4. |  |  |  | 9. |  |  |  | 14. |  |  |  |  | 19.
| 5. |  |  |  | 10. |  |  |  | 15. |  |  |  |  | 20.
I guarantee that i will follow the rules, mentioned on the precautions part of risk assesment form, and also under negative conditions i will stop working in a safe way,then inform my project manager

## 16 Step 4 Approval Mgmt
| Pathway of activity / | Assessment / Değerlendirme High (H) / Yüksek (Y) Medium (M) / Orta (O) Low (L) / Düşük (D) |  |  | Precautions |  |  | Assessment / Değerlendirme High (H)
No |  | Likelihood (L) | Severity (S) | Risk Score(R) |  |  |  | Likeliho od (L) | Severity (S) |  | Risk Score(R)
STEP 4 / | APPROVAL / ONAY - EHS MANAGER & SITE MANAGER
| EHS MANAGER | [5 empty] | SITE MANAGER
Approval / Onay | Name Surname: |  |  |  |  | SUITABLE | Name Surname: |  |  | SUITABLE
| Date: | [5 empty] | Date:
| Signature |  |  |  |  | UNSUITABLE | Signature |  |  | UNSUITABLE
| Phone | [5 empty] | Phone